Validation of Coupled Neutronic /

Thermal-Hydraulic Codes for VVER Reactors

VALCO

CO-ORDINATOR

Forschungszentrum  Rossendorf e.V., FZR

Institut für Sicherheitsforschung

P.O.B. 510119

D - 01314 Dresden

GERMANY

Tel.:	+ 49 351 260 3480

Fax:	+ 49 351 260 3440

LIST OF PARTNERS

1. Gesellschaft für Anlagen- und Reaktorsicherheit (GRS) mbH, Germany

2. Technical Research Centre of Finland, VTT, Finland

3. KFKI Atomic Energy Research Institute, AEKI, Hungary

4. Nuclear Research Institute Rez, plc, NRI, Czech Republic

5. VUJE Trnava a.s., Slovakia

6. Institute for Nuclear Research and Nuclear Energy, INRNE, Bulgaria

7. State Scientific and Technical Centre on Nuclear and Radiation Safety, SSTCNRS, Ukraine

8. SE, a.s.EBO, o.z., Jaslovské Bohunice, Slovakia

9. SE, a.s.EBO, o.z., Mochovce, Slovakia

10. Russian Research Center “Kurchatov Institute”, KI,  Russia

CONTRACT N°:	FIKS-CT-2001-00166

EC Contribution:							EUR    672,902

Total Project Value:							EUR  1,043,331

Starting Date:								January 1, 2002

Duration:								30 months

CONTENTS

LIST OF ABBREVIATIONS AND SYMBOLS	3

EXECUTIVE SUMMARY	4

A. OBJECTIVES AND SCOPE	5

B. WORK PROGRAMME	6

B.1 Extended validation of coupled codes (WP 1)	6

B.2 Comprehensive uncertainty analysis for coupled codes (WP 2)	7

B.3 Specific validation of neutron-kinetic models (WP 3)	7

C. WORK PERFORMED AND RESULTS	8

C.1 State-of-the-Art Report	8

C.1.1 Coupled Codes	8

C.1.2 Uncertainty analysis	11

C.1.3 Neutron-kinetic codes	11

C.2 Extended validation of coupled codes (WP 1)	12

C.2.1 Acquisition and selection of transients for validation	12

C.2.1.1 The VVER-440 transients	13

C.2.1.1.1 NPP Bohunice-3	13

C.2.1.1.2 NPP Mochovce-2	13

C.2.1.1.3 NPP Dukovany-2	13

C.2.1.2 The VVER-1000 transients	14

C.2.1.2.1 NPP Kozloduy-6	14

C.2.1.2.2 NPP Rivne-3	14

C.2.2 Results of the Bohunice-3VVER-440 transient calculations	15

C.2.2.1 Calculation specification	15

C.2.2.2 Used codes and assumptions	15

C.2.2.3 Bohunice results	15

C.2.3 Results of the Kozloduy-6 VVER-1000 transient calculations	16

C.2.3.1 Used codes and assumptions	17

C.2.3.2 Kozloduy results	17

C.3 Comprehensive uncertainty analysis (WP 2)	18

C.3.1 GRS methodology for uncertainty and sensitivity analysis	18

C.3.2 Analysis of the Loviisa-1 transient (VVER-440)	19

C.3.2.1 Description of the transient	19

C.3.2.2 Main physical phenomena during the transient	19

C.3.2.3 Determination of uncertain parameters, parameter ranges and distributions	19

C.3.2.4 Description of simulation codes and used input decks	20

C.3.2.5 Evaluation of the calculation results	20

C.3.2.6 Discussion of sensitivity analysis	20

C.3.2.7 Discussion of upper and lower limit values	21

C.3.2.8 Summary of the results for the Loviisa-1 transient	21

C.3.3 Analysis of Balakovo-4 transient (VVER-1000)	22

C.3.3.1 Description of the transient	22

C.3.3.2 Main physical phenomena during the transient	22

C.3.3.3 Determination of uncertain parameters, parameter ranges and distributions	22

C.3.3.4 Description of simulation codes and used input decks	22

C.3.3.5 Evaluation of calculation results	23

C.3.3.6 Discussion of sensitivity analysis	23

C.3.3.7 Discussion of upper and lower limit values	24

C.3.3.8 Summary of results for the Balakovo-4 transient	24

C.4 Validation of neutron-kinetic models (WP 3)	24

C.4.1 Measurements in the V-1000 facility	24

C.4.1.1 The test facility	24

C.4.1.2 Survey of experiments selected for VALCO	25

C.4.2 Generation of the nuclear input data for the neutron-kinetic codes	25

C.4.2.1 Two-group nuclear data for the fuel assemblies	25

C.4.2.2 Reflector data	26

C.4.3 V-1000 steady state calculations	26

C.4.3.1 Steady-state measurements in the V-1000 Facility	26

C.4.3.2 Core power distribution in un-rodded V-1000 steady state	26

C.4.3.3 Power distribution in V-1000 steady state with group 10 inserted	27

C.4.3.4 Assembly pin power distributions	27

C.4.3.5 Multiplication factors	28

C.4.3.6 Code verification against two-dimensional V-1000 benchmark	28

C.4.4 V-1000 transient calculations	29

C.4.4.1 Transient measurements	29

C.4.4.2 Insertion of single control rod cluster	30

C.4.4.3 Reactor scram	30

CONCLUSION – PROSPECTIVE VIEWS	31

EUROPEAN ADDED VALUE	34

REFERENCES	34

TABLES	40

FIGURES	46

# LIST OF ABBREVIATIONS AND SYMBOLS

ADF	assembly discontinuity factor

CR	control rod

FA	fuel assembly

k-eff	effective multiplication factor

KNK-56	type name of out-core ionisation chambers

LR0	zero-power reactor of Nuclear Research Institute Rez, near Prague

LOCA	loss-of-coolant accident

LWR	light-water reactor

MCP	main circulation pump

NPP	nuclear power plant

PIR	type name of reactimeters

PRZ	pressurizer

PSA	probabilistic safety analysis

PWR	pressurized water reactor

RCC	rank correlation coefficient

RDF	reference discontinuity factor, applied for non-multiplying material

RMS	root of mean square

RPV	reactor pressure vessel

P	relative power density

SA	sensitivity analysis

SG	steam generator

SPND	self-powered neutron detector

UA	uncertainty analysis

UASA	uncertainty and sensitivity analysis

VVER	pressurized water reactor designed in Russia (water/water energetic reactor)

ZPCF	zero-power critical facility

ßeff	effective fraction of delayed neutrons

r	reactivity

r0	initial reactivity

# EXECUTIVE SUMMARY

The VALCO project aims at the improvement of the validation of coupled neutron-kinetic / thermal-hydraulic codes for VVER reactors. VALCO was started January 1, 2002 and was completed June 30, 2004.

A major objective of VALCO was to study the ability of codes to model the NPP behaviour in different types of transients. For this reason in work package 1 (WP 1), the existing data base, containing already measured VVER transient data from the former EU Phare project SRR-1/95, has been extended by five new transients. Two of these transients ‘Drop of control rod at nominal power at Bohunice-3’ of VVER-440 type and ‘Coast-down of 1 from 3 working MCPs at Kozloduy-6’ of VVER-1000 type, were then utilised for code validation. Eight institutes contributed to the validation with ten calculations using five different combinations of coupled codes. The thermal-hydraulic codes were ATHLET, SMABRE and RELAP5 and the neutron kinetic codes DYN3D, HEXTRAN, KIKO3D and BIPR-8. The general behaviour of both the transients was quite well calculated with all the codes.

In VALCO work package 2 (WP 2), the usual application of coupled neutron-kinetic / thermal-hydraulic codes to VVER has been supplemented by systematic uncertainty and sensitivity analyses. A respective method was applied to the two transients studied earlier in SRR-1/95: A load drop of one turbo-generator in Loviisa-1 (VVER-440), and a switch-off of one feed water pump in Balakovo-4 (VVER-1000). Results have been obtained by applying different coupled code systems (SMABRE – HEXTRAN, ATHLET – DYN3D, ATHLET – KIKO3D, ATHLET – BIPR-8). An essential result of the analysis is the identification of the input parameters that most sensitively affect safety-relevant output parameters. Uncertainty bands for these output parameters have been derived. The variation of potentially uncertain input parameter values as a consequence of uncertain knowledge can activate system actions causing quite different transient evolutions.

Results of SRR-1/95 coupled code analyses led to the objective to separate neutron kinetics from thermal-hydraulic feedback effects. Thus, in VALCO work package 3 (WP 3) stand-alone three-dimensional neutron-kinetic codes have been validated. Measurements carried out in an original-size VVER-1000 mock-up (V-1000 facility, Kurchatov Institute Moscow) were used for the validation of the codes DYN3D, HEXTRAN, KIKO3D and BIPR-8.  The significant neutron flux tilt measured in the V-1000 core, caused only by radial-reflector asymmetries, was successfully modelled. A good agreement between calculated and measured steady-state powers has been achieved, for relative assembly powers and inner-assembly pin power distributions. Calculated effective multiplication factors exceed unity in all cases. The time behaviour of local powers, measured during two transients that were initiated by control rod moving in a slightly super-critical core, has been well simulated by the neutron-kinetic codes.

In all, the results of the VALCO project represent a successful validation and verification of different neutron-kinetic / thermal-hydraulic codes designed and used for safety analyses in Russian VVER-440 and VVER-1000. The VALCO teamwork has contributed to deepening East-West European co-operation on nuclear reactor safety.

# A. 	OBJECTIVES AND SCOPE

Modern safety standards for nuclear power plants (NPP) require the modelling of complex transients where there is a strong interaction between the thermal-hydraulic system behaviour and the space-dependent neutron kinetics. Therefore, the current VALCO project has been established for the improvement of the validation status of coupled neutronic / thermal-hydraulic codes, especially for Russian VVER reactors. The codes need to be validated against well-specified transient scenarios.

VALCO is partially based on results obtained earlier for VVER-440 and VVER-1000 within the EU Phare project SRR-1/95 (Ref. [1,2]). Two selected transients, one for either VVER type, were analysed in this former project by different coupled code systems. The calculated results were compared with measured transient data from original NPPs. The objective of Work Package 1, led by VTT, was therefore to extend and qualify the measurement data base and to expand the validation of coupled codes.

The SRR-1/95 transient analyses suggested that uncertainties of given input information are responsible for deviations. In order to quantify the implications of input uncertainties on calculation results, an uncertainty analysis method has been applied for coupled codes. This is the main objective of Work Package 2, carried out under the leadership of GRS. The members of the VALCO project should get familiar how to perform such an analysis based on the GRS SUSA method.

Both transients studied in the former SRR-1/95 project have shown deviations in the calculated reactor powers. They must have been caused by differences in the neutronic data (control rod efficiencies) and / or in the dynamic thermal physics of the applied fuel rod models affecting the Doppler feedback. To separate the pure neutron-kinetic effects from feedback effects, a specific validation of neutron kinetics (”neutronics”) models was to be performed in Work Package 3, led by FZR, by simulating steady states and transients measured in the V-1000 zero-power test facility of the Kurchatov Institute Moscow. The V-1000 data are considered a unique material for the validation of neutron-kinetic codes for hexagonal fuel assembly geometry.

The VALCO project is aimed at the improvement of methods and analytical tools for addressing operational safety issues particularly for VVER type reactors. Recently, in the countries of Central and Eastern Europe (CEE) and the independent States (CIS) of the former Soviet Union, where nuclear power plants with VVER type reactors are exploited, different operational concepts for improving effectiveness were implemented, e.g. advanced fuel cycles or upgrading of power. For the purpose of the verification of the plant behaviour in the new conditions, independent code systems, which have been carefully validated, are needed by the nuclear authority organisations during the licence processes.

# B. 	WORK PROGRAMME

## B.1 	Extended validation of coupled codes (WP 1)

In the framework of the completed Phare project SRR-1/95 a measurement data base about transient processes at NPPs with VVER type reactors had been set up. In particular, the description of the following transient processes were provided:

	for VVER-440:	–	drop of one turbine to the power station internal load level at the Loviisa-1 NPP,

- –	shutdown of 3 from 6 working main coolant pumps at the Dukovany-2 NPP and

	for VVER-1000:	–	turn-off of one from two working SG feed water pumps at the Balakovo-4 NPP,

–	decrease of the turbo-generator power from 1000 MW down to the power station internal load level at the Zaporoshye NPP,

–	switch-off of two neighbouring main coolant pumps at the Kozloduy NPP.

The transients measured in Loviisa-1 and Balakovo-4 were analysed by different neutronics / thermal hydraulics coupled codes. For the other transients, all relevant plant data and available measurement parameters were documented for future analyses.

While the transients analysed in Phare SRR-1/95 were initiated by perturbations in the secondary circuit, transients triggered by actions in the primary circuit, e.g. switching-off main coolant pumps, are of special interest in the current project. The initial task in Work Package 1 of VALCO is to collect and document more VVER transient data for the validation of coupled codes. The analyses of new transients had to be performed with the following coupled codes: DYN3D-ATHLET, KIKO3D-ATHLET, BIPR-8-ATHLET, HEXTRAN-SMABRE, and DYN3D-RELAP.

## B.2 	Comprehensive uncertainty analysis for coupled codes (WP 2)

The previous transient analyses (Phare SRR-1/95) have shown that the results of calculations depend on various input parameters of the codes, model options, nodalisation etc. On the one hand, different physical model parameters have caused deviations between the different code options. On the other hand, differences in the results of transient analyses were observed, when calculations were performed by using the same code system and input deck, but by different users. These findings gave rise to adapting and applying an uncertainty analysis method for coupled codes.

The two plant transients analysed in Phare SRR-1/95 are to be studied by the SUSA method: the load drop of one turbo-generator in Loviisa-1, a VVER-440 plant, and the switch-off of one feed water pump in Balakovo-4, a VVER-1000 plant. The first step of the uncertainty analysis is to identify and quantify all potentially important input parameters including their uncertainty bands and probability distributions. On this basis the statistical package SUSA has to be used to generate by Monte Carlo methods a set of input parameter values.

The computer codes to be applied are the thermal-hydraulic code ATHLET coupled with different 3D-neutronic models such as DYN3D (FZR, NRI, SSTCNRS), KIKO3D (AEKI), and BIPR-8 (KI), as well as the coupled thermal-hydraulic / 3D-neutronic code SMABRE-HEXTRAN (VTT). For comparison, GRS has to perform calculations by ATHLET with point kinetics. The propagation of the input uncertainties through the code runs should provide the related probability (uncertainty) distributions for the code results.

## B.3 	Specific validation of neutron-kinetic models (WP 3)

To separate the pure neutron-kinetic effects from feedback effects, a specific validation of neutron-kinetic (”neutronic”) models is to be performed by the calculation of kinetic experiments, carried out in the V-1000 zero power test facility of the Kurchatov Institute Moscow. Data from several measurements are available.

In a first validation step, measured V-1000 steady-state power distributions can be used to validate the three-dimensional two-group diffusion models, which form the ”stationary kernels” of the respective neutron-kinetic (dynamic) codes applied in the transient calculations. Results of two transient experiments carried out in the V-1000 zero power test facility have to be made available, in which different control rods were moved.

These steady states and transients are to be calculated by the three-dimensional neutron kinetic codes DYN3D, HEXTRAN, KIKO3D, and BIPR-8. Prior to these calculations, libraries of two-group diffusion and kinetics parameters, which are input to the neutronic codes, have to be generated by multi-group transport lattice codes for the V-1000 fuel assemblies as well as for the radial and axial reflectors of the core.

# C. WORK PERFORMED AND RESULTS

## C.1 	State-of-the-Art Report

### C.1.1 	Coupled Codes

New challenges concerning the accuracy and reliability of prediction in transient analysis can only be met using coupled code systems. The new challenges are due to the fact, that in recent years the scope of accident analysis was extended from LOCA and RIA to transient scenarios, where a very tight coupling of the thermal hydraulics of the plant with the neutronic behaviour of the reactor core is very important. Such kinds of transients and accidents are:

- over-cooling transients caused by leakages in the steam system e.g. main steam line break scenarios,

- boron dilution scenarios,

- accident scenarios with anticipated failure of the reactor scram (ATWS),

- neutronic/thermal-hydraulic instabilities in boiling water reactors (BWR).

Therefore, a broad spectrum of code systems with coupling of thermal-hydraulic plant models and 3D neutron-kinetic codes has been developed worldwide, mainly within the last decade. These code systems are more and more used to perform the analysis of accident scenarios. They replace the use of traditional thermal-hydraulic system codes like ATHLET or RELAP5 with point models of neutron kinetics or of stand-alone core models, where the boundary conditions have to be provided separately.

The coupled code systems have the following advantages [3]:

- The effects of feedback of thermal hydraulics on neutron kinetics behaviour are described consistently with high accuracy.

- The interaction between the reactor core behaviour and the behaviour of other nuclear plant components (primary circuit, secondary circuit, plant control system) is considered in a realistic way.

- Within 3D neutron kinetics there is no need to determine reactivity coefficients, as they are necessary for low-dimensional models, and to show their conservatism.

- The conservatism of the analyses can in general be reduced. This is especially important, because nuclear power plants are nowadays operating closer to power limits relevant for nuclear safety.

The coupled code systems have mainly been developed by inter-connecting existing thermal-hydraulic system codes and 3D neutron-kinetic models. The system codes, mostly one-dimensional, comprise the solution of the mass, energy and momentum balance equations of two-phase flows, additional models for single effects like critical discharge or level formation and special component models e.g. for pumps, steam generators, and pressurizers. Moreover, they contain balance-of-plant models, which are able to describe control actions like reactor scram, power control, control of thermal-hydraulic parameters like feed water temperature, steam pressure, the activation of valves, switches or auxiliary systems. Some system codes contain 3D thermal-hydraulic models for selected zones like reactor core or RPV, mostly in porous media approach with coarse nodalisation [4].

The 3D neutron kinetics models are mostly based on nodal expansion methods (NEM) within neutron diffusion theory. The macroscopic cross sections in the diffusion codes depend on the feedback parameters like fuel temperature, moderator density and temperature, which, on the other hand, depend on the power density. Therefore, the interaction between thermal-hydraulic plant behaviour and neutron kinetics is consistently described in the coupled codes. Another important feedback parameter in PWR is the boron concentration.

The well-known and widely distributed thermal-hydraulic system codes like RELAP, CATHARE, TRAC and ATHLET have been coupled in recent years with various 3D neutron-kinetic models. State-of-the-art reviews on coupled code systems are given e.g. in [4] and [3]. Various neutron-kinetic codes, namely the codes BIPR-8, KIKO3D, DYN3D and QUABOX/CUBBOX are coupled to ATHLET [3,5]. Basic features of these codes, coupling techniques and applications for plant transient analyses are described in [5].

Different coupling techniques are used for the connection of neutronic models to system codes. The spectrum of techniques ranges from a straight-forward explicit coupling with alternating call of the sub-codes over an iterative coupling via special interfaces for data exchange until full integration of the 3D neutron kinetic modules into the system code [3,4,6].

Two different basic ways of coupling are described in these references. One of them is the so-called internal coupling, where the modules of the neutronic code are directly implemented into the thermal-hydraulic system code, replacing e.g. corresponding point kinetics or 1D kinetics subroutines. The thermal-hydraulic behaviour of all components of the plant including the reactor core is modelled by the system code. Thermal-hydraulic feedback parameters for each node are transferred to the neutron kinetic model, and power densities are transferred back from the neutronic model for each heat conduction object in the system code’s nodalisation scheme. The internal coupling technique is the most consistent way of coupling. Advantages and disadvantages of the coupling strategies will be described later.

An alternative coupling technique is external coupling. The reactor core is completely modelled by the 3D reactor-dynamic model, including thermal hydraulics. The system code models the whole plant thermal hydraulics except the reactor core. Core inlet and outlet boundary conditions are exchanged between the two sub-models. External coupling is easy to implement, however in some cases, it may lead to unstable numerics, especially in cases with strong coupling between thermal hydraulics and neutronics, e.g. for BWR. This was the reason to develop a third type of coupling, the so-called parallel coupling. In this approach, the thermal-hydraulic behaviour is completely modelled by the system code. This provides stability of thermal-hydraulic calculation, depending on the robustness of the system code itself.  Boundary conditions at the core inlet are provided to the reactor core model. The reactor core behaviour, including thermal hydraulics, is described by the core model. Thermal-hydraulic parameters calculated by the core model are used to get the feedback to neutron kinetics. Parallel coupling joins the advantages of internal and external coupling (numerical stability, rather easy to implement), but inconsistencies might occur between the two different thermal-hydraulic models applied for the core.

Advantages of the different coupling strategies are the following:

- Internal coupling is the most consistent approach, but requires significant modifications in the two codes.

- External coupling is relatively easy to implement. The maintenance of both codes can be performed independently from each other. External coupling is easy to update for newly released code versions.

- Using external coupling, a large number of parallel thermal-hydraulic channels in the core can easily be treated (1:1 assignment of fuel elements to channels).  For most of the system codes, the treatment of a large number of parallel channels leads to numerical problems or very high computation times.

Advantages and disadvantages (with respect to application) are determined by the features of different thermal-hydraulic core models. The thermal-hydraulic model of DYN3D, for example, is not capable of treating the formation of a water level in the core or global reversal of coolant flow direction as it can occur during LOCA. On the other hand, DYN3D comprises a rather detailed model of fuel rod behaviour, which is able to estimate the change of the heat transfer coefficient in the gas gap during transients.

Concerning the validation of coupled code systems, large efforts have been made recently. Significant progress has been achieved in the validation of thermal-hydraulic system codes against experiments in thermal-hydraulic test facilities, on the one hand, and of neutron-kinetic models against kinetics measurements in zero-power reactors. Restrictions and shortcomings of the thermal-hydraulic codes have been identified mainly in the modelling of components or effects, where 1D thermal hydraulics is not sufficient (horizontal steam generators, RPV, stratification in horizontal pipes, turbulent mixing). Corresponding research projects to improve the capabilities of thermal-hydraulic codes by implementing 3D approaches are in progress.  One contribution is also given in the VALCO project by the development of ATHLET models with very detailed steam generator and RPV nodalisation, which is practically equivalent to the 3D porous-body approach.

To separate neutronics from thermal-hydraulic effects in the coupled code validation, additional validation of 3D neutron kinetics models is performed within VALCO, based on conclusions drawn from the EU Phare project SRR-1/95 [7].

However, for the validation of the coupled codes as a whole, data are needed from experiments, where both thermal hydraulics and neutron kinetics are relevant. These data can practically only be gained from real transients in NPP, because thermal-hydraulic test facilities do not allow modelling feedback effects, on the one hand, and zero-power reactors, where neutronic measurements can be performed with sufficient accuracy, do not show thermal-hydraulic effects because of very low heat release, on the other hand. However, measurement data from NPP are only available for transients close to operational conditions. For this reason, the coupled code validation on international benchmark tasks is a necessary complementary activity. A series of OECD benchmarks for PWR, BWR and VVER-1000 is performed [8, 9, 10]. Benchmarks on overcooling transients for VVER-440 reactors have also been organised within “Atomic Energy Research” (AER), an international association on physics and reactor safety of Russian VVER [11, 12]. A comprehensive validation of coupled codes was performed, based on real VVER transients [13, 7]. This validation work was continued in a systematic way within the VALCO project.

### C.1.2 	Uncertainty analysis

Usually, the analysis of transient scenarios with respect to reactor safety is performed using the conservative approach. Codes are applied, which contain intentionally conservative methods, e.g. overestimation of break flow rate or decay heat release estimation at upper bound in LOCA analysis. Additionally, “pessimistic” assumptions for the initial and boundary conditions are made. The problem of conservative approach is, that the conservatism cannot always definitively be shown. Moreover, conservatism depends on the process to be analysed. An assumption or model can lead to conservative results for one kind of transients and to non-conservative ones for another class of scenarios.

Therefore, recently best-estimate methods are used for safety analysis increasingly. In the so-called best-estimate approach, codes and methods are applied that do not contain any intended conservatism. The simulation of transients and accident scenarios is based on methods, which comprise the best status of knowledge presently available. As it was outlined in Chapter C.1.1, the application of coupled codes is a best-estimate approach providing realistic, consistent results and reducing the conservatism of the safety assessment. However, even a best-estimate analysis contains uncertainties due to uncertain knowledge of input parameter values and the validity of sub-models. For application of best-estimate analyses, uncertainty analysis is requested e.g. in the US Nuclear Regulatory Guide. The uncertainty analysis (UA) provides quantitative information about the effect of that uncertainty on output results and the sensitivity analysis (SA) finds the major sources responsible for that uncertainty. With the help of UA, the upper bound of a time-dependent curve of safety-relevant parameters can be assessed, which is not exceeded with a certain, high probability. This upper bounded curve can be compared with safety limits. SA can be used to identify weak points, where reduction of deficiencies in knowledge is most important to increase the accuracy of the results of the analyses. Therefore, uncertainty and safety analysis (UASA) is an important tool of safety assessment to be combined with coupled code analyses.

A comprehensive overview on UASA methods is given in [14]. Problems of uncertainty analysis are also treated in [4]. Among others, there are statistical UASA methods, where a well-defined set of calculations of a transient is performed with statistical variation of input parameters and model parameter settings. Based on the results of these calculations, UA and SA are performed using statistical analysis. One of these statistical methods is the SUSA method developed by GRS.

Usually, statistical UASA methods have been applied for thermal-hydraulic LOCA analyses. However, they are of general nature and can be applied to any kind of calculation analysis. In the VALCO project, the SUSA method has been used to produce uncertainty bands for comparison with measurement data. It has been extended to coupled-code applications including uncertain parameters of the reactor core physics model.

### C.1.3 	Neutron-kinetic codes

In current LWR calculations of core time-dependent spatial neutron flux distributions, usually the 3D neutron diffusion equation is solved, based on two energy groups with six groups of delayed neutron precursors. This approach has been proven to be adequate for steady state and transient applications in uranium-fuelled PWR, including the VVER under consideration in the VALCO project. It is realized that the utilisation of MOX fuel with higher contents of plutonium will require more than two neutron energy groups.

Most of the currently applied neutron-kinetic (neutronic) codes allow the calculation of effective multiplication factors k-eff, 3D transient flux (power) distributions, xenon transients, depletion, and pin power recovery. Different approaches are used to solve the neutron diffusion equation, such as nodal methods (applying transverse integration or flux expansion), finite-difference and finite-elements methods. A survey of the approaches is given in the final report on Work Package 2 of the EU FP5 CRISSUE-S project [4]. Nodal methods are widely applied, which is also true for the current project. The reactor core is divided into so-called nodes, i.e. volume elements (prisms) that are determined by the structure of the fuel assemblies. Thus, node-homogenized neutron-diffusion and kinetics parameters are to be provided as input. Most of the codes allow the application of ADFs to reduce homogenisation errors.

The following items may require further investigation, cf. also [4]:

-	Identification of a suitable number of neutron energy groups,

-	Influence of resonance absorption cross sections in ‘individual’ layers of pellets (partly connected with the previous item),

-	Systematic identification of influence of material discontinuities, e.g. due to the presence of burnable absorbers, control rods, VVER-440 special control assemblies and discontinuities at the border between reflector and core,

-	Pin power recovery in nodal codes for VVER.

The last two items are addressed in the present VALCO project. Details about the neutronic codes involved in VALCO and their coupling to thermal-hydraulic system codes are described in [15-25].

## C.2 	Extended validation of coupled codes (WP 1)

### C.2.1 	Acquisition and selection of transients for validation

Data was collected from five transients, three concerning VVER-440 plants and two of VVER-1000 type. One VVER-440 case and one VVER-1000 case were then chosen for validation: ‘Drop of control rod at nominal power at Bohunice-3’ for VVER-440 reactors and ‘Coast-down of 1 from 3 working MCPs at Kozloduy-6’ for VVER-1000 reactors. The former is an unexpected event focusing on core power and RPV mixing phenomena, whereas the latter is part of start up tests and emphasizes loop thermal hydraulics.

Eight institutes participated in the code validation with five different coupled codes. Six teams applied ATHLET as thermal-hydraulic code and five teams DYN3D as neutronics code. The combination of ATHLET and DYN3D was applied by four teams. The participants, codes and calculated transients are summarized in Table I.

#### C.2.1.1 	The VVER-440 transients

##### C.2.1.1.1 NPP Bohunice-3

In the Bohunice unit 3, control rod No. 287 from group 2 dropped during normal full power operation 6.1.1999 [26]. The power at first decreased to 89% Nnom. The protection system prevented full power recovery by blocking control group withdrawal. The operator then reduced the power to 85% Nnom, where all the parameters were stabilised. The first 1000 seconds after rod drop are interesting for the code validation.

The external ionization chamber recordings showed that the power distribution was remarkably skewed. This is also reflected in a variation of hot leg temperatures, fuel assembly outlet temperatures and self powered neutron detector (SPND) signals. The observed phenomena enable model evaluation of reactivity effects of rod movements and consequent power redistribution calculations. The changes in the hot leg temperatures also allow an evaluation of mixing process in the upper plenum.

##### C.2.1.1.2 NPP Mochovce-2

In the NPP Mochovce unit 2 the main coolant pumps No. 1, 3 and 5 were disconnected during a slow power rise [27]. The protection system AO-3 was activated (slow shutdown by insertion of control rod groups in sequence). The pressure in main steam collector varied between 4.30 and 4.51 MPa during the transient process. The unit power was reduced to 47% Nnom. The powers of turbo generators were reduced to 89MW and 101MW. A maximum of coolant heat up on assembly was 38°C.

The data set gathered is extensive. The pump trip transient is fairly fast and in that sense also suitable for validation calculation. The primary and secondary circuit phenomena are covered extensively in the data. The core neutron power signals are also included to monitor the power behaviour during the transient.

##### C.2.1.1.3 NPP Dukovany-2

A transient occurred at Dukovany NPP Unit 2 December 19th 1997 in full power operation during maintenance of the feed water control valve units [28]. During the maintenance fault feed water control signals were generated, which influenced the steam generators’ (SG) level control in the first phase of the transient. The control system could not balance the SG surfaces, which first led to slow shutdown mode of the reactor (AZ-3). The levels of two adjacent SGs continued to fall and the operator switched off their MCPs and increased the feed water supply to them. The levels of these two SGs started to rise. One of them, however, reached a too high level, which launched a turbine trip and consequently a reactor scram (AZ-1).

The main plant components for a system simulation are described in detail, as well as the initial plant conditions and the time course of transient parameters. The length of the transient is reasonably short - less than 15 minutes from the beginning of the initiating event.

#### C.2.1.2 The VVER-1000 transients

##### C.2.1.2.1 NPP Kozloduy-6

In the first phase, MCP No. 3 was switched off at full power, after which the automatic reactor power regulator decreased power to about 65 % and the flow in the tripped loop reversed [29]. In the second phase, 90 minutes later, MCP No. 1 was tripped, after which also this loop reversed. The regulator reduced reactor power further to 51.5 % by first moving the control rod group No. 10 in and half a minute later out. The primary pressure was regulated by the feed-and-bleed system and experienced a temporary rise of max 0.25 MPa during 40 - 160 s, when flow reversed in the tripped loop. The pressurizer spray valve opened twice. The steam header pressure decreased by max 0.07 MPa during 20 – 80 s but was also recovered. The turbine controller unloaded the turbine from 565 MW to 415 MW within 60 s. The time-dependent core data was limited, but the initial and final states of the transients were documented. The plant functions and measurements were documented extensively and sometimes, in case of conflicting information, additional data evaluation effort was needed.

##### C.2.1.2.2 NPP Rivne-3

The experimental information on control rod movements have been documented on tests, that were carried out at unit 3 of the Rivne NPP of VVER-1000/V-320 type during start-up of the 14th fuel cycle, February 14th 2001 [30]. In the beginning of each fuel cycle the NPP staff performs tests to prove coincidence between calculations and operational safety-relevant parameters of the reactor core, as well as to check the right connection of the thermocouples and the self-powered neutron detectors (SPND) to the core monitoring system. The experiment for correct sensor connections is performed at 80 % power level, which is achieved in 10-12 h when starting from zero power. Hence, xenon-135 distribution has not yet stabilised in the beginning of experiment. To check the correct sensor connections one of the 61 control rods is inserted into the core from the upper position down to the bottom. After 2-3 minutes the thermocouple and SPND readings are recorded, after which this control rod is withdrawn from the reactor core. Such a procedure is repeated for some control rods located at different positions of the core. The maximum variation of the recorded neutron power in this data set was from 80 % to 74% Nnom.

A considerable amount of data is provided, such as reactor core loading in 360-symmetry (asymmetric loading), axial burnup distribution, reactor power history to calculate the xenon-135 distribution before the experiment, control-rod-position changes, neutron power changes, reactivity changes, SPND and thermocouples readings, and key thermal-hydraulic parameters. The operational history from three previous cycles has also been provided in order to enable independent burnup calculations.

### C.2.2 	Results of the Bohunice-3VVER-440 transient calculations

#### C.2.2.1 Calculation specification

The calculated transient starts with control rod drop during the first 12 seconds. The initial position of the regulating group was 175 cm from the bottom of the core. The operator gradually lowered the power level from 89 % to 85 % by moving downward the regulating group, but the needed movement was not reported. For the calculations the regulating group was recommended to be inserted in two slopes (1/4 and 3/4 of the total movement) within fixed time periods that seemed to fit best with the data. The determination of the absolute movement was left for the analysis teams. Also the modelling flow by-pass routes had to be agreed upon to enable fuel assembly outlet temperature comparisons. No recommendations were given for the secondary side modelling, because the level of detail varied a lot between the teams.

#### C.2.2.2 Used codes and assumptions

The Bohunice transient was calculated in five institutes [31-35] with five different code couplings (Table I). All teams modelled all the fuel assemblies separately, but the amount of thermal-hydraulic channels in the core region varied. Most of the teams also modelled all the six circulating loops individually.

The asymmetric transient also appears in the loop behaviour, and hence mixing in the lower and upper plenum calls for attention. VTT, KFKI and KI applied specific mixing models for these volumes, while NRI and VUJE assumed perfect mixing. In the core mixing is very limited due to the shrouds around the assemblies.

Four lattice codes, CASMO-4, HELIOS, KARATE-440 and KASSETA were used for cross section data preparation from the nuclear data libraries.

#### C.2.2.3 Bohunice results

The rod drop is immediately recorded by the out-core ionization chambers close to the dropped rod. The plant data is presented as stepwise signals, where the reading is updated only when the change is large enough from the previous value. In the modelling VTT applied specific response kernels for the out-core neutron detectors, while the rest simulated the signal with fast neutron flux in the fuel nodes closest to the detector location. All the simulations of the close detectors at first go below the recorded relative power 0.7, but then recover on some higher level due to feedback effects. The other detectors record only the later control action and set close to 0.9. The overall asymmetry of the core at the end of the calculation is illustrated in Figure 1. It appears that the calculated relative radial power profiles vary considerably close to the dropped rod (±10 %), which may also be seen in the simulated external detector signals. This may imply that modelling of the VVER-440 type control rods in nodal codes still needs attention.

The codes predict power levels from 90 to 95 % after the initial drop. The KFKI, VUJE and NRI calculations stay at a higher level than the VTT and KI calculations. The variation can be explained by differences in feedback models such as fuel Doppler effect and worth of the dropped rod. In the KFKI and VUJE calculations the core inlet temperatures decrease more and thus increase reactivity in the core compared to other calculations.

The final power level of 85 % was then obtained by moving the regulating group downwards. In the simulations the regulating movement varied considerably, ranging from 12.4 cm to 29.5 cm. The main reason for the differences is the varying intermediate power level after the rod drop, but other modelling parameters also contribute, such as the reactivity effects of fuel temperature, coolant inlet temperature and the worth of the regulating group.

The kernel model of the ionization chambers softens the simulated signal compared to the simpler fast flux of the closest fuel node (Figure 1): In the VTT calculation the power after the rod drop is the smallest and the radial power tilt one of the largest, but the simulated signal of the closest detector EP1 is in the middle of the other calculations.

The measured hot leg temperatures start to diverge just after the rod drop due to asymmetric power generation. In the VTT and KFKI calculations the upper plenum is modelled without mixing and in the lower plenum only with partial mixing. In these results the hot leg temperatures in the two loops near the dropped rod decrease 7 °C more than in the opposite loops, which is in agreement with the observation. In the KI result the divergence is 4 °C, while in the other calculations with perfect mixing the phenomenon is naturally lost.

An example for the fuel assembly outlet temperatures during the transient is shown in Figure 2. The measured temperature decrease close to the dropped rod, 17 °C, is a bit larger than the simulations. The KFKI and VTT results are closest to the measurements. The temperature drop due to the later control action is somewhat larger in the calculations than in the measurements. Naturally, the temperature decrease is much smaller far from the dropped rod, which is well described by the codes.

In the Bohunice core there are Rhodium type SPNDs at seven elevations in 36 fuel assemblies. The signals of eight assemblies were compared to the measurements. The signals decrease almost uniformly near the dropped rod at all elevations, by 0.55 in relative units. On the other side of the core the rod drop is not seen, but only the later control action. The general behaviour of the calculated SPND signals is quite well in accordance with the measurements.

### C.2.3	Results of the Kozloduy-6 VVER-1000 transient calculations

An experiment of two successive pump trips was conducted in the start-up tests of the Kozloduy NPP unit 6 of VVER-1000/V-320 type in 1992. In the VALCO project only the latter trip was chosen for code validation.

#### C.2.3.1 	Used codes and assumptions

The Kozloduy transient was calculated in five institutes, at VTT, KI, FZR, SSTCNRS, and INRNE [36-40] with three different coupled codes. The used codes are summarised in Table I. All code-coupling types were in use. This kind of transient needs modelling of all the circulation loops, but symmetry of the core may be applied. Only KI used the whole core modelling. The intermediate time of 90 minutes is not quite enough to stabilize the whole primary system, but such an assumption may be used in the calculations, except for the core xenon content.

#### C.2.3.2 Kozloduy results

For power regulation FZR, SSTCNRS and INRNE used measured CR positions directly as boundary condition, whereas VTT simplified it slightly and KI modelled the controller itself. The core power is measured only a few times (Figure 3). Generally the calculations follow the real behaviour, even though there is some underestimation during the stabilization phase. The differences between the measurements and the calculations are largest before the control group withdrawal at 40 s.

In the simulation of flow behaviour, it is important to model flow friction in different parts of the primary circuit properly, and to use as correct homologous pump curves as possible. The data included measured pressure differences during normal operation and some characteristic pump coast down curves, but plant-specific pump curves were not available. Some generally used models in VVER-1000 applications could, however, be obtained. Based on this material, it was the responsibility of each team to prepare the model. The measured and calculated pressure differences over the MCPs are compared in Figure 4. It may be noticed that the general behaviour during the transient is well reproduced, but some deviations appear, such as the higher than measured pressure differences in the running pumps of SSTCNRS and VTT or the slightly deviating time behaviour of the FZR pumps. Also the calculated core mass flows and loop flows that are derived from the pressure differences, may deviate as much as 10 % from the evaluated data. The timing of flow reversal varies between 38.6 s of SSTCNRS to 50 s of FZR.

The cold leg temperature is controlled by the secondary temperature until the flow is reversed. The reversal brings about a temperature minimum in the cold leg, the depth of which varied from 5 to 10 ºC in the calculations. In the beginning most of the calculations were in accordance with the measured cold leg temperature and at the end all except KI are about 2 °C below the measurements. The INRNE calculation started from a lower level mainly because of the larger total flow. The hot leg temperature of the affected loop experiences a stronger and permanent decrease.

In the evaluation of upper plenum pressure and pressurizer level, it turned out that all the calculated pressures are more sensitive than the measurement to changes in the primary loop just after MCP trip, which often appears in one-dimensional modelling of multidimensional phenomena. Further, the primary feed and bleed and spray valve flows were compared.

The level of detail in the secondary side modelling varied also in the Kozloduy transient. As an example, FZR, SSTCNRS and INRNE used the measured steam header pressure as a boundary condition. Several secondary side parameters were included in the data comparison to check proper boundary conditions for the primary side that was in the focus of this study. Most of the parameters were in reasonable agreement with the observations.

The axial and radial power distribution and the core outlet temperature distributions were compared in the initial and final state. The simulation of a xenon transient between the two pump stops by VTT and SSTCNRS leads to more downwards peaked power profiles than in the other calculations. In the FZR and INRNE initial states the xenon change is compensated with increased boric acid concentration. The applied boron concentration varied between the calculations due to some ambiguity in the plant data [29].

The initial and final radial power distributions were also compared to plant data. In the initial state the calculations differed from the measurements on an average by more than 5 % (KI result 3.4 %). In the final state the results are better. In all the calculations the largest differences are in the middle of the core.

The calculated core outlet temperatures are systematically higher than the measured ones. The difference between the calculations and the measurements seems to depend on bundle power. The phenomenon is even more pronounced at the end of the transient with smaller mass flow and larger temperature rise in the core. This could possibly be explained by the location of the thermocouple in the mid line of the bundle below the conical part of the bundle head. The measurement could be at least partly disturbed by the colder water coming from the central tube.

## C.3 	Comprehensive uncertainty analysis (WP 2)

### C.3.1 	GRS methodology for uncertainty and sensitivity analysis

Results from applications of complex computer models are subject to uncertainty due to “lack of knowledge” of parameter values and sub-models. The uncertainty analysis (UA) provides quantitative information about the effect of that uncertainty on output results and the sensitivity analysis (SA) finds the major sources responsible for that uncertainty.

The principal steps of the Uncertainty and Sensitivity Analysis (UASA) are:

1.	identify the problem and the computer model to treat it,

2.	identify all relevant sources of “lack of knowledge” uncertainty and represent them by uncertain parameters,

3.	specify probability distributions for the parameters to quantify the “state of knowledge” uncertainty on parameter level,

4.	from these distributions generate a random sample of size N of parameter values,

5.	perform N model runs with these parameter values as input,

6.	derive quantitative statements on the output uncertainty (UA),

7.	compute sensitivity measures (SA),

8.	analyze, discuss and interpret the results.

These steps are explained in more detail in [41,42]. The method was applied for two plant transients. The results obtained are briefly presented in the following sections, a complete documentation is given in [42].

### C.3.2 	Analysis of the Loviisa-1 transient (VVER-440)

#### C.3.2.1 	Description of the transient

The experiment of a load drop of one turbo-generator was carried out at Loviisa-1 NPP after a power increase of the plant to 1500 MW. A detailed description of the plant transient and results from analyses by coupled codes are provided in [2]. The reactor was operated at nominal power, and the transient was initiated by the load drop of one turbo-generator. That means the electric power output was suddenly reduced by half. Shortly after the load drop the reactor control system started to reduce the reactor power by inserting the control rod group six, which is normally used for power control. When the reactor power reached 84 % of nominal power, the automatic power control system was erroneously switched off. Therefore, the further power reduction to 60 % within about 100 s was manually controlled by the operator.

As a result of the power reduction, the coolant temperatures of the hot legs decreased. Moreover, the cooling of the primary circuit through the steam generators was reduced because of increasing steam pressure at the secondary side. Therefore, the cold leg temperatures increased significantly. About 20 s later, the temperatures at cold leg also followed the decrease of hot leg temperatures. On the secondary side, at first, the pressure started to increase sharply, but it was quickly brought back to normal conditions by opening the turbine bypass valves. Afterwards, the secondary side conditions were adjusted to the reduced nuclear power.

#### C.3.2.2 	Main physical phenomena during the transient

The sequence of events for the load drop transient is given in Table II. The corresponding changes of the plant conditions are summarized in Table III.

#### C.3.2.3 	Determination of uncertain parameters, parameter ranges and distributions

The evaluation of the transient evolution and the discussion of the possible effect of model parameters or system actions led to the identification of uncertain factors. These model parameters are compiled in Table IV.

On the basis of the investigation of the physical processes, possible sources of uncertainties were determined leading to the list of uncertain parameters (Table V). In technical discussions using expert knowledge about the processes and the plant features the range of the parameter values together with the probability distributions were determined, too.

#### C.3.2.4 	Description of simulation codes and used input decks

Calculations have been performed by five working groups applying different code systems. The working groups and their simulation codes are summarized in Table VI. The working groups perform the calculations not only by using different code systems, but also with different models of the plant configuration.

As different computer codes have been applied to the same problem, the study allows uncertainty and sensitivity analyses of the plant transient and a comparison between the different simulation models and their effect on the results, as well.

#### C.3.2.5 	Evaluation of the calculation results

For the evaluation of the results of the uncertainty and sensitivity analysis the following six main output parameters were chosen:

- Relative core power

- Coolant temperature at inlet of hot leg

- Coolant temperature at outlet of cold leg

- Pressure at inlet of hot leg

- Mass flow at inlet of hot leg

- Level in the pressurizer

Time functions of relative core power for two sets of calculations are presented as an example (Figures 5-6). These are the point kinetics calculations performed by GRS, and HEXTRAN/SMABRE calculations by VTT. The complete set of figures for all six main output parameters of all calculations is provided in [42].

#### C.3.2.6 	Discussion of sensitivity analysis

The sensitivity analysis for the effect of uncertain parameters on the uncertainty of results is discussed here. The corresponding numbering of uncertain parameters, as defined in Table V, is as follows:

P1 – Function of secondary pressure, 
P2 – Model for control rod insertion, 
P3 – Total reactivity of control rod group, 
P4 – Shape of axial burn-up distribution, 
P5 – Mass flow rate between upper head and upper plenum, 
P6 – Operation of make-up system, 
P7 – Heat-up time constant of heaters in pressurizer, 
P8 – Total heating power of heaters in pressurizer, 
P9 – Fuel rod gap heat transfer coefficient, 
P10 – Core bypass, 
P11 – Correction of Doppler effect, 
P12 – Correction of moderator density effect.

Figures 7-8 show the results of the sensitivity analysis of the two sets of calculations mentioned in the previous section. Each curve in the corresponding figure presents the time-dependent rank correlation coefficient (RCC) during the transient, which is a measure for the relative importance of the uncertainty of the input parameter on the uncertainty of the investigated output parameter at the time t. The time dependence of these coefficients reflects the changes of their relative importance during the transient. Due to the sample size N=100, a rank correlation coefficient with an absolute value below 0.2 must be considered statistically not significant. The sign of the coefficient indicates whether the positive change of the uncertain input value has a positive or negative effect on the output value.

For each output parameter the most sensitive parameters were identified. Mostly, these were the function of the secondary pressure (P1) and the type of control rod insertion (P2).

#### C.3.2.7 	Discussion of upper and lower limit values

From the calculation results, two-sided upper and lower tolerance limits (= tolerance intervals) are determined for the coverage =90% and the confidence level =95%. The time functions of the reference solution with the tolerance limits are determined for all output parameters, defined in section C.3.2.5. As an example, the relative core power for two sets of calculations is shown (Figures 9-10). The measured data are also included in the figures. The corresponding band represents the uncertainty of results as a consequence of the variation of input parameters.

#### C.3.2.8 	Summary of the results for the Loviisa-1 transient

The plant transient after a load drop of one turbo-generator at the Loviisa-1 NPP was analysed by five working groups applying different code systems. A common list of uncertain parameters was specified along with parameter ranges and probability distributions over these ranges. This specification and quantification of uncertainty was the basis to generate the input parameter values for 100 simulation runs from which a random sample of the code results has been obtained. Generally, the uncertainty and sensitivity results were quite consistent for the different code systems. The most sensitive input and model parameters that were identified by the statistical analysis are all physically reasonable and typical for the particular transient. It is the time function of the secondary pressure and the effectiveness and the way of how control rods are inserted to reduce power. The analysis allowed determining the upper and lower tolerance limit values for the relevant parameters of the solutions due to the uncertainties in the input of the codes. Comparing these limit values with the measured data and the reference solutions demonstrates the agreement between solutions and real plant behaviour. It presents very well what could be achieved by further improving the input values of the models.

### C.3.3 	Analysis of Balakovo-4 transient (VVER-1000)

#### C.3.3.1 	Description of the transient

During a test in Balakovo-4 NPP, one of two working main feed water pumps was switched off at nominal power. A detailed description of the plant transient and results from analyses by coupled codes are described in [1]. Two seconds after the pump switch-off, the power control system responded by inserting the control rod group K1 from top to bottom within four seconds. As a result the neutron power decreased to about 63 % of nominal power within 10 s. Also the control rod group K10 started moving in at a rate of 2 cm/s. The initial axial position was at 275 cm. The slow insertion of control rod group K10 down to an axial position of 140 cm resulted in further power decreasing to about 45 % of nominal power.

The reactor power was stabilized at this level by the automatic power control. As all four main coolant pumps continued operation, the differences between the temperatures of the hot legs and the corresponding cold legs of the four primary loops decreased proportionally to the thermal power reduction.

In the secondary side, the feed water flow rate through the second feed water pump, which was still in operation, increased by about 50 % within 16 s after the initiating event in order to compensate partly the deficient feed water flow. In the following, the flow rate of this second feed water pump was reduced again to match the reduced thermal power of the primary circuit. During the whole transient, the water levels in the steam generators were always kept well above the heater tubes.

#### C.3.3.2 	Main physical phenomena during the transient

The sequence of events for the transient is given in Table VII. The corresponding changes of the plant conditions are summarized in Table VIII.

#### C.3.3.3 	Determination of uncertain parameters, parameter ranges and distributions

The investigation of physical processes and the identification of possible sources of uncertainties led to the list of uncertain parameters compiled in Table IX. Based on technical discussions and plant features, ranges of parameter values and probability distributions were determined, too.

#### C.3.3.4 	Description of simulation codes and used input decks

Calculations have been carried out by four working groups applying different code systems. The groups and their simulation codes are summarized in Table X.

The working groups perform calculations with different models of the plant configuration. The primary circuit of a VVER-1000 consisting of four loops and corresponding steam generators is modelled in different degree of detail in the single input decks.

As different computer codes have been applied to the same problem, the study allows uncertainty and sensitivity analyses of the plant transient and a comparison between the different simulation models and their effect on the results, as well.

#### C.3.3.5 	Evaluation of calculation results

For the evaluation of the obtained results the following seven main output parameters were chosen:

- Relative core power

- Coolant temperature at inlet of hot leg

- Coolant temperature at outlet of cold leg

- Pressure at upper plenum

- Mass flow at inlet of hot leg

- Level in the pressurizer

- Mixture level in the steam generator

A complete set of figures for all seven selected output parameters from all four sets of calculations can be found in [42]. No figures for this plant transient are presented here for brevity.

#### C.3.3.6 	Discussion of sensitivity analysis

The corresponding numbering of uncertain parameters, as defined in Table IX, is as follows:

P1 – Function of secondary pressure, 
P2 – Total reactivity worth of control rod group K1, 
P3 – Total reactivity worth of control rod group K10, 
P4 – Shape of axial burnup distribution, 
P5 – Fuel temperature feedback, 
P6 – Moderator density feedback, 
P7 – Heat-up time constant of heaters in pressurizer, 
P8 – Protection of heaters in pressurizer, 
P9 – Fuel rod heat transfer coefficient, 
P10 – Mass flow of the feed water, 
P11 – Enthalpy of feed water.

For each output parameter the most sensitive parameters were identified. Mostly, these were the function of the secondary pressure (P1) and the reactivity feedback coefficients (P5 and P6).

#### C.3.3.7 	Discussion of upper and lower limit values

From the calculation results, two-sided upper and lower tolerance limits (= tolerance intervals) are determined for the coverage =90% and the confidence level =95%. The time functions of the reference solution with the tolerance limits are determined for all output parameters, defined in section C.3.3.5.

#### C.3.3.8 	Summary of results for the Balakovo-4 transient

The plant transient that was initiated in Balakovo-4 NPP by a switch-off of one of two working main feed water pumps was analysed by four working groups applying different code systems. A common list of uncertain parameters was specified along with parameter ranges and probability distributions over these ranges. This specification and quantification was the basis to generate the input parameter values for 100 simulation runs, from which a random sample of the code results has been obtained. The analysis of this plant transient differs from the previous Loviisa-1 case, because varying transient courses are produced here by the initiation of different actions (e.g. reactor trip or switching off main coolant pumps). The simulation models represent the NPP including all limitation and protection systems. Due to the variations of input parameters, the transient evolution after the initiating event varies, leading to actions that did not occur under the conditions of the plant experiment. In this way the uncertainty and sensitivity analysis reveals the spectrum of possible transient evolutions. The analysis cannot be restricted to the particular transient as observed during the test. The differences between the four sets of solutions are mainly caused by the fact that the simulation models lead to different types of actions or, at least, to different time points. Considering this aspect, the uncertainty and sensitivity results were quite consistent for the different code systems. The most sensitive input and model parameters that were identified by the statistical analysis are all physically reasonable and typical for the particular transient. The most sensitive parameters are those, which determine the power reduction in the initial phase and the power generation at the new stable plant condition, i.e. the moderator density feedback and the fuel temperature feedback.

The analysis has allowed determining the upper and lower tolerance limit values for the relevant parameters of the solutions, due to the uncertainties in the input of the codes. Comparing these limit values with the measured data and reference solutions demonstrates the agreement between solutions and real plant behaviour.

## C.4 	Validation of neutron-kinetic models (WP 3)

### C.4.1 	Measurements in the V-1000 facility

#### C.4.1.1 	The test facility

The zero-power critical facility V-1000 (ZPCF V-1000, cf. [43]) has been used as a full-scale mock-up of the Russian VVER-1000 core; i.e. a V-1000 core was built of 163 original VVER-1000 fuel assemblies and the 61 standard control rod clusters, each consisting of 18 absorber rods. The hexagonal assembly lattice pitch is 23.6 cm, the 312 fuel rods being 353 centimetres long (active length).

A VVER-1000 radial reflector of stainless steel is placed around the core. This reflector is provided with vertical cylindrical holes at several positions, i.e. drillings through the whole reflector height. Twelve 70-mm-diameter drillings, located only at the “south-west” 60-degree sector of the radial reflector, are plugged with 65-mm-diameter stainless-steel bolts. The ring-shaped gaps around these plugs are filled with moderator. Ionisation chambers (KNK-56) for out-core neutron flux measurements are inserted into two other (oppositely located) dry 75-mm-diameter drillings. There are moderator-filled gaps between the 90 outer fuel assembly faces and the radial reflector (baffle), varying between 1.7 mm and 5.4 mm. The space between the baffle and the reactor tank, simulating the VVER-1000 down-comer, is also filled with moderator.

#### C.4.1.2 	Survey of experiments selected for VALCO

All measurements have been carried out in a fresh core representing the original first loading of a three-year VVER-1000 fuel cycle, the boric-acid-water-solution moderator being at room temperature, which is extremely cold compared to a PWR. Criticality was achieved by slowly rising the moderator level in the core.

Table XI gives a survey of the four V-1000 states studied in VALCO [44]. In the first two states, stationary power distributions have been measured, which are suitable for the validation of the steady-state kernels of neutron-kinetic codes. Starting from the steady states No. 3 and 4, transients were initiated by movement of CR clusters. Most of the data measured during these two kinetic experiments have been applied to validate the reactor-dynamic parts of the codes.

### C.4.2 	Generation of the nuclear input data for the neutron-kinetic codes

#### C.4.2.1 	Two-group nuclear data for the fuel assemblies

Two-group diffusion and kinetic parameters for the V-1000 fuel assemblies are needed as input for the neutron-kinetic codes to be validated. Thus the validation includes the lattice codes used for the generation of these nuclear data. Libraries containing node-homogenized parameters have been generated by Serco Assurance (United Kingdom), VTT (Finland), INRNE (Bulgaria), KI (Russia), and SSTCNRS (Ukraine), applying the standard lattice codes WIMS8 [45], CASMO-4 [46], HELIOS-1.5 [47], TVS-M [48], and NESSEL-4 [49], respectively.

#### C.4.2.2 	Reflector data

The power distribution in the above-described cold V-1000 core turned out to be very sensitive to radial reflector properties. Thus, extra attention has been paid to an accurate calculation of albedos describing the neutron reflection at the radial edge of the core.

The first step in calculating the radial boundary conditions is to prepare multi-group transport cross sections, including P1-scattering matrices, for all materials in the problem solved. At this stage the lattice code HELIOS-1.5 and its 90-group nuclear data library have been used, cf. [50]. 23-group transport cross sections have been generated for the fuel, cladding, and moderator materials in each fuel cell, for the absorber, absorber cladding, guiding tube, and moderator materials in each absorber cell, etc. for each assembly type in asymptotic surrounding. Also 23-group cross sections for the moderator and steel materials in the radial reflector have been calculated by using an extended assembly gap around a single fuel assembly, which includes layers of moderator and steel similar to the real reflector arrangement.

The second step is to solve the neutron transport equation in 23 groups for the real two-dimensional heterogeneous geometry by the neutron transport code MARIKO [51]. A 60-degree sector of the core with rotational symmetry is considered. The converged transport solution is used to set up inhomogeneous boundary value problems for the radial reflector only, which are solved again by MARIKO in order to calculate the accurate 2-group (group to group) albedo boundary conditions for each assembly face on the core-reflector boundary.

### C.4.3 	V-1000 steady state calculations

#### C.4.3.1 	Steady-state measurements in the V-1000 Facility

Core power distributions were measured by irradiation of special short fuel rods that had been inserted into the central tubes of the fuel assemblies (FA). The short fuel rods, being only 50 cm long, there middles placed at 120 cm from the fuel bottom of the core, were used as γ-activation detectors, thus yielding the radial power distribution at this height. The powers of standard fuel pins in one assembly (3 positions to the right of the central assembly) were measured, too, after dismantling it, by detecting the radioactivity levels of selected single fuel pins.

The following steady states are available for comparison with calculations [44]:

-	V-1000 state with all control rods of group 10 fully inserted (No. 1 in Table XI),

-	V-1000 state without any control rods inserted (No. 2 in Table XI).

#### C.4.3.2 	Core power distribution in un-rodded V-1000 steady state

Figure 11 gives an idea of the relative power density measured in the second steady state described in Table XI, with all control rod groups fully driven out of the core. Although the core is symmetrically loaded (60-degree rotational symmetry), a power tilt is observed. This tilt can only be caused by asymmetries in the radial reflector, such as the plugged drillings and different moderator gaps between core and radial reflector. As indicated in the previous section, relative central pin powers have been measured, and such powers should be calculated by the codes for comparison. From the nodal reactor-dynamic codes to be validated, DYN3D (FZR) enables calculating pin powers by pin power recovery (see section C.4.3.4), otherwise only node-averaged powers, computed at the height position of the measuring central-channel short fuel rods, can be provided. Naturally, the deviations of the normalized node-averaged powers are higher than those of the central pin values. The root-of-mean-square (RMS) deviations are about 5 % and 3 % for the DYN3D node-averaged and central pin results, respectively (cf. [52, 53]). Similar deviations have been observed for the results calculated by the nodal reactor-dynamic code BIPR-8 [54] (node-averaged) and the stationary heterogeneous fine-mesh four-group code PERMAK, cf. [49], (central pin).

In Figure 12, respective node-averaged results by the reactor-dynamic codes HEXTRAN (VTT, [55]), KIKO3D (AEKI, [56]), and BIPR-8 (KI, [54]) are shown together with the DYN3D deviations. The codes applied the HELIOS-generated fuel assembly two-group data [57] and albedos generated by MARIKO [58]. Only in the BIPR-8 calculations, PERMAK-generated reflector data have been used. Table XII gives a survey of maximum and mean deviations. The RMS deviations are roughly the same in all four cases. Using NESSEL assembly data does not very much change the deviations. However, as shown in [53], NESSEL-generated radial boundary conditions would lead to clearly higher discrepancies, due to the NESSEL model, which is not accurate enough for the complex VVER-1000 radial reflector.

Deviations of node-averaged results by HEXTRAN (VTT) applying MARIKO-generated albedos, but different sets of fuel-assembly two-group data are compiled in Table XIII. The agreement between calculated and measured power distributions is roughly the same with the different data sets. A similar pattern is observed for DYN3D results with different sets of two-group data [52].

#### C.4.3.3 	Power distribution in V-1000 steady state with group 10 inserted

A heavy over-estimation of the measured powers by the node-averaged powers is observed in the six assemblies where the control rods of group 10 are fully inserted. This discrepancy is due to the neutron absorption by the control rods surrounding the measuring central short fuel rod. Naturally, calculating the power in the central pin by pin-power recovery improves the agreement. The RMS deviations obtained by DYN3D for the central pin powers with the HELIOS, CASMO, and WIMS [59] data are 4.2 %, 6.2 %, and 5.0 %, respectively. Similar agreement has been reached by PERMAK using TVS-M data [54].

#### C.4.3.4 	Assembly pin power distributions

The pin power measurement of the dismantled fuel assembly, mentioned in C.4.3.1, provides one more opportunity of validating the DYN3D flux reconstruction method [60] in combination with pin powers from the HELIOS cell calculations. For the steady state with all control rods out, the maximum deviation is 4.0 %, the RMS deviation 1.4 %. It is the same level of agreement as reached in heterogeneous calculations by steady-state fine-mesh codes such as HEX2DB using HELIOS data [57] and PERMAK / TVS-M [54]. The inner-assembly power tilt reaching more than a factor 2 from the left to the right assembly edge, is well described.

The configuration with inserted absorber rods (group 10) represents a greater challenge for the pin power recovery, compared to the un-rodded case, because of increased heterogeneity and therefore higher inner-assembly flux gradients. The maximum deviation by DYN3D is 8.9 % (RMS deviation 3.7%). The fine-mesh codes HEX2DB and PERMAK, both applying heterogeneous (i.e. non-homogenized) diffusion parameters within the fuel assemblies, produce similar maximum deviations of 8.6 % and 9.8 %, respectively.

#### C.4.3.5 	Multiplication factors

The calculations for the steady states (and for all combinations of neutronic codes and data libraries) over-estimate criticality by 500-1700 pcm. WIMS-based calculations yield the greatest surplus, about 500 pcm systematically higher than those based on other two-group data. The deviations of the effective multiplication factors k-eff from unity can be partly due to measurement errors of the boric acid concentration, estimated by the KI experimenters to reach ±0.3 gram boric acid per kilogram water; which corresponds to an uncertainty of about ±600 pcm in k-eff. Furthermore, the overestimation is systematically higher by some 300 pcm in the case with control rod group 10 inserted, compared to the un-rodded state. Unfortunately, the two steady states had different boric-acid concentrations, both values being independently affected by the high measurement error. The experimenters should rather have provided for exactly the same boric acid concentration (without exactly knowing it, of course) in both states. In this case, clearer conclusions about the rod efficiency of group 10 in connection with the critical moderator level could have been drawn.

Different nodal codes using the same two-group diffusion data produce code-to-code deviations in k-eff of up to ~200 pcm. This is interesting in connection with the benchmark results discussed at the end of next section.

#### C.4.3.6 	Code verification against two-dimensional V-1000 benchmark

The relative deviations between calculated and measured powers reach 10 % and more, even in the un-rodded state described in section C.4.3.2. Uncertainties in the radial reflector geometry may be partly responsible for the discrepancies. On the other hand, while power distributions in usual VVER-1000 operational states are rather smooth, the cold-core steady state depicted in Figure 11 shows enormous spatial power variations, posing a challenge to nodal codes. For this reason, a heterogeneous V-1000 benchmark, tailored to this measured state, has been established, in order to quantify the mere implications of homogenisation effects (homogenized two-group diffusion parameters being used by the neutronic codes) and the nodal diffusion approximation on the accuracy of calculated power distributions and multiplication factors.

The two-dimensional 60-degree-core-sector heterogeneous 23-group transport-theory benchmark solution has been calculated by the transport code MARIKO [57]. This type of benchmark can be considered an “ideal experiment” being clear of any measurement uncertainties.

The nodal reactor-dynamic codes DYN3D (FZR), HEXTRAN (VTT), and the nodal stationary code SPPS (INRNE, [57]) have been verified against the benchmark. In this benchmark, as in the real 360-degree power distribution that had been measured at room temperature in the V-1000 facility, the assembly power varies by a factor 20. There is a high relative deviation up to 9 % at the centre of core, although the absolute deviation in this place is small - only 0.01 - in the distribution normalized to unity. Taking into account the fact, that “in real life”, there are additional sources of error, such as uncertainties in the nuclear data processed in the lattice calculations, as well as V-1000 measuring errors, the power deviations of 10% or higher, as seen in Figure 12, are plausible. Usually, i.e. in normal reactor operation states with much smaller radial flux gradients, the nodal codes perform better.

The codes under consideration have originally been designed for VVER-440 analyses. A sufficient accuracy for the hexagonal mesh size of 14.7 cm, given by the VVER-440 fuel assembly dimensions, has been demonstrated e.g. for DYN3D in [16, 61]. For the larger VVER-1000 assembly size of 23.6 cm, the codes are not too accurate, as it seems, for core states with high flux gradients. Thus, the DYN3D nodal model has been refined [15]. While in the original model DYN3D(HEXNEM1), as used in the present V-1000 calculations, the hexagonal nodes are coupled by averaged partial currents through node sides, in the refined HEXNEM2 method, additional node coupling through hexagon corners is considered. Accuracy has been further improved by introducing two-group diffusion parameters for hexagonal radial-reflector nodes, including reference discontinuity factors (RDFs) [61], which show advantages over conventional albedos. Applying these improved methods reduces the maximum relative error from 9 % to 2.5 %. By the same token, the error of the effective multiplication factor (k-eff) is reduced from about 200 pcm to some 30 pcm.

### C.4.4 	V-1000 transient calculations

#### C.4.4.1 	Transient measurements

Two transients measured in the V-1000 facility have been applied for the validation of reactor-dynamic codes. They were both initiated by control rod movements [44] and started from steady states with asymmetric power distributions, due to asymmetries in the radial reflector (cf. section C.4.3). The exact transient initial conditions are compiled in Table XI (states No. 3 and 4). Short fuel rods were not present. Instead, micro fission chambers (diameter: 7 mm, active length: 5 mm) had been placed in the central channels of eight fuel assemblies, in order to measure the relative power change as a function of time in these positions. The fission chambers were placed at the distances of 285 cm, 175 cm, or 85 cm from the fuel bottom. Reactivities were determined by two reactimeters, PIR1 and PIR2, applying inverse point kinetics to the signals of respective out-core ionisation chambers KNK-56, placed at opposite sides of the radial core edge.

In the first V-1000 dynamic experiment, a single control rod cluster was inserted and then withdrawn. The second transient was a reactor scram with one control cluster being first stuck in a middle position and then also inserted.

#### C.4.4.2 	Insertion of single control rod cluster

A single control rod cluster of group 9 (near to the core periphery) was inserted within 80 s (transient time 16–96 s) and later withdrawn (800–837 s). Before the transient, the reactor had been supercritical by the reactivity of 25 pcm, measured by the reactimeters. The transient was simulated by different codes, taking into account this initial reactivity. Various sets of two-group neutronic data have been applied.

Neutron-kinetic codes enable estimating the dynamic reactivity from core-averaged fluxes. Averaged values of delayed-neutron parameters (determined from steady state fluxes) are used. All codes yield practically the same time course.  Asymptotically, i.e. about 400 s after the rod movement, when local effects of the reactimeters have become irrelevant, there is a good agreement between the results of the codes and both reactimeters. The asymptotic values of the dynamic reactivity for the inserted cluster (reduced by the initial value) and the corresponding rod worth (near 70 pcm) obtained from steady state calculations are in good agreement, the relative deviation is 3 % and less.

Figure 13 gives an example for local power densities measured by the micro-fission-chamber detectors. Node-averaged powers normalized to their initial values have been calculated by different nodal reactor-dynamic codes. All codes well describe the course of local power densities at different detector positions, the HEXTRAN-HELIOS results being nearest to the measurement. KIKO3D-HELIOS and DYN3D-HELIOS curves are very close to each other, both somewhat underestimating the measurement. Using the other libraries of two-group diffusion and kinetics parameters, produced by CASMO, WIMS, and NESSEL, gives a similar quality of agreement as that seen in Figure 13.

HELIOS-produced data tend to over-estimate the rod efficiency of the inserted cluster. The WIMS- and NESSEL-based rod efficiencies are also higher than those of CASMO. Their effect on the power curves, however, is mostly compensated by higher values of ßeff, which also leads to a somewhat better description of the power time behaviour than HELIOS-based calculations.

It has been shown by DYN3D-NESSEL calculations [53] that wrong radial core boundary conditions leading to a symmetric power distribution in the steady state before the transient – thus ignoring the measured radial power tilt (see Figure 11) - strongly affect rod efficiency. In such symmetric conditions, the efficiency of the control rod cluster in FA 126 would reach only about 55 pcm instead of much more realistic 70 pcm.

#### C.4.4.3 	Reactor scram

Starting from the steady state described by the last row of Table XI, all control rod clusters except one of group 9 were fully inserted within 4 s. The stuck cluster was only slowly inserted down to a position of 183.6 cm (measured from core fuel bottom) within 34.5 s, and kept there up to 282 s. Then, it was fully inserted within 35 s (282 – 317 s). The reactor was supercritical before the experiment with a reactivity of 11.5 pcm.

Figure 14 depicts the measured and calculated power densities in the assembly with the stuck cluster. Node-averaged powers normalized to their initial values have again been calculated by the nodal reactor-dynamic codes, all using the same HELIOS library. The control rods reach the detector height position just at the end of transient, as seen in the calculations. In the scrammed reactor, the measurement of power densities becomes more and more inaccurate during the transient evolving, due to the very low detector counting rates (statistics). Nevertheless, relative powers have been measured up to about 200 seconds, and the course of decreasing power is described by the codes.

Normalized fast fluxes averaged over the peripheral assemble pairs, adjacent to the two out-core ionization chambers, have been calculated and compared to the respective ionisation chamber signals. A good description of the measurement by all combinations of codes and two-group parameters has been observed. For both ionization chambers, HEXTRAN-HELIOS, DYN3D-CASMO, and DYN3D-WIMS produce curves that are practically identical.

# CONCLUSION – PROSPECTIVE VIEWS

The amount of data from NPP transients, available and suitable for code validation, is restricted. Moreover, the instrumentation of operating nuclear power plants is not primarily designed for measuring data to be used for coupled-code validation. Nevertheless, all available information of several VVER transients has been gathered and carefully documented in VALCO WP 1, in accordance with "best practice guidelines" for validation and verification test cases, as outlined in the EU FP5 ECORA report [62].

In the calculation of the Bohunice VVER-440 transient, the most essential part for validation is the core behaviour during the control assembly drop and three minutes later starting control actions to reach 85 % power level. The general behaviour during the whole transient was quite well calculated with all the codes: both the power distribution changes and the fuel assembly outlet temperatures were mostly well reproduced. There were, however, notable differences in the first power decrease, in the axial power profile, in the calculated control assembly worth and in the fuel temperatures. The differences in the required control group movement to reach the final power were large between several calculations, which may be due to the models applied to the fuel rods as well as to the VVER-440 control assemblies. It is recommended to improve the VVER-440 control-assembly models implemented in the neutron-kinetic codes under consideration. They should be validated against measurements in a suitable zero-power facility. In principle, the LR0 facility of NRI Rez will fit for this purpose. These investigations may be performed within EU FP6 NURESIM.

The high time constants observed in the Bohunice SPND measurements remain an open issue. Possibly, un-documented manual operator actions may be responsible.

The measurements of the individual assembly outlet temperatures and the hot leg temperatures indicated that in the transient the coolant mixing in the upper plenum was weak. This could also be demonstrated with the codes that included a mixing model and a detailed enough core channel description.

The features that make the Kozloduy VVER-1000 transient interesting, such as lowered power and flow reversals in the loops, also proved to be difficult both for data collection and for modelling. As an example, it was very hard to find detailed enough data about pump characteristics and control logics. Several versions of pump models generally used in VVER-1000 calculations were available. Based on this material, it was the responsibility of each team to prepare the model. Anyway, the general behaviour of the Kozloduy second pump trip was calculated satisfactorily with all the codes.

In the comparison of the core outlet temperatures, a linear dependency was found between the assembly power and the difference between measured and the calculated temperatures. The dependency could possibly be explained by a bypass flow through the bundle central tube.

Furthermore, in the Kozloduy calculations the initial fuel temperatures and the temperature changes during the transient vary remarkably between the different codes. This supports the conclusion of the previous SRR-1/95 project that more accurate fuel models are needed in the codes.

In all, the comparison between the codes and the validation against measurements was successful and the results were reasonably accurate. The VALCO participants learned that careful plant data interpretation and balanced plant modelling is important, especially for transients where asymmetric phenomena are dominant.

The studies performed in WP 2 demonstrated that the GRS uncertainty and sensitivity method is applicable to coupled code calculations. The amount of necessary simulation runs and corresponding computing times are affordable. No internal code adjustments are needed. The results from the different code systems are quite consistent in view of the relevant dependencies of results on the input parameters. The results can be used to estimate on a proven statistical basis the lower and upper tolerance limit values, which express the variation of results as a consequence of the specified uncertainty.

The results of the sensitivity analysis gave indications to parameters for which the uncertainty of knowledge should be reduced in order to reduce the uncertainty of results most effectively. In some uncertainty calculations, even a reactor trip has been observed, which was not expected. Those cases may be of special worth for the uncertainty assessment, because it is revealed how the transient could have alternatively developed.

In all, the GRS uncertainty and sensitivity analysis method based on the SUSA package was successfully applied to both SRR-1/95 transients. It will be necessary, however, to get more experience for the uncertainty and sensitivity of results for safety relevant transients. Each transient defines particular requirements in view of the uncertainty of model parameters. The modelling of NPP should be as complete as possible, including the plant-specific control and protection system. Results of uncertainty and sensitivity analyses are most valuable to define safety margins against acceptance criteria.

In WP 1 and WP 2, three different types of coupling the thermal-hydraulic system codes with the core models have been applied:

-	internal coupling,

-	external coupling,

-	parallel coupling.

For the transients under consideration in both work packages, all three types of coupling have been applied and provided results that agree with the measurement in the range of uncertainty. Differences between calculation results are not caused by the type of coupling, but by different physical models within the codes and different modelling approaches.

In VALCO WP 3, the stand-alone neutronic codes have been successfully validated against V-1000 (zero power) measurements. The effect of a strong steady-state radial power tilt, measured in the V-1000 core, is described by all codes, when the real boundary conditions (albedos) are applied. These albedos are based on the accurate reflector model, including different water gap widths between fuel assemblies and steel baffle. The powers calculated for the central pins give better agreement with measurements than the node-averaged values, particularly for nodes with control rods inserted. The pin power calculation for assembly 85 is in good agreement with measured pin power distributions. The effective multiplication factor was over-estimated in all calculations by (0.5 … 1.7) %. One reason may be in the error of the boric-acid concentration measurement, which leads to an uncertainty of  0.6 % in k-eff. Another source of uncertainty can be errors in the two-group diffusion parameters for the very low operation temperatures in the V-1000 facility.

Code validation against experiments is always complicated by measurement errors (cf. also EU FP5 ECORA report [62]). For this reason, the nodal diffusion (neutronic) codes, applying homogenized two-group parameters have been additionally verified against a heterogeneous multi-group transport-theory benchmark, which can be considered an “ideal experiment” being clear of any measurement uncertainties. This benchmark test was successful and in accordance with the steady-state validation results.

Concerning the first V-1000 transient experiment, where one single control rod cluster was moved, it can be stated that all combinations of neutron-kinetic codes and two-group-parameter libraries successfully simulate the time behaviour of the measured relative power densities (micro fission chambers) and fast-neutron fluxes (ionisation chambers). The rod worth, calculated for the single cluster as the difference in k-eff for this cluster totally inserted and totally withdrawn, is close to the asymptotic value of the measured and calculated dynamic reactivity.

Regarding the second transient experiment, a scram with one stuck cluster being later inserted, the calculated results are also close to the detector signals, taking into account the greater statistical errors of the measurement in the scrammed reactor.

The validation against measurements in the Moscow V-1000 facility has demonstrated that the neutron-kinetic codes are suitable for the calculation of power distributions and power changes caused by control rod movements in a real VVER-1000. Pin power recovery is necessary to describe the central-channel measurements in strongly heterogeneous fuel assemblies. To cope with the over-estimation of the effective multiplication factor, some adjustment of two-group diffusion parameters may be necessary in practical VVER-1000 calculations.

# EUROPEAN ADDED VALUE

The documentation of the five transients, measured in operating VVER-440 and VVER-1000 nuclear power plants, is one of the most valuable results achieved in VALCO work package 1. Measurements performed in the full-scale VVER-1000 mock-up in Moscow (V-1000 facility), which have been documented in work package 3, are also useful for further code validation. The transient documentations can be used also by institutions that did not participate in VALCO. The use of the measured transient data for further validation work is restricted to VALCO members.

The extension of uncertainty analyses to coupled code calculations, and the respective experience gathered in work package 2 for Russian VVER, may be helpful for similar accident analyses of other European PWR or BWR.

Most of the archived measured VVER and V-1000 data, as well as the results of code validation and uncertainty analyses should be interesting for code users, especially in organizations of VVER-operating countries. As already practiced in the foregoing EU Phare SRR-1/95 project, the nuclear authorities of those countries shall have access to the VALCO documents. In this sense, VALCO contributes to the improvement of the reliability and accuracy of VVER safety assessment.

The experience from VALCO work package 3 has led to a fruitful cooperation between the two European organizations INRNE (Bulgaria) and FZR (Germany), resulting in an improvement of accuracy in the VVER calculations by the neutron-kinetic code DYN3D. Benchmark tests have shown that the improved methods allow a more accurate calculation of VVER cores and safety-relevant parameters. Respective results and data will be made available to the DYN3D users in 7 European countries.

In all, the VALCO teamwork has contributed to deepening European co-operation on nuclear reactor safety, especially for Russian VVER-440 and VVER-1000 reactors, which are operated in countries of Northern, Central and Eastern Europe and in several Independent States of the former Soviet Union.

# REFERENCES

[1]	Mittag, S., Kliem, S., Weiss, F. P., Kyrki-Rajamäki, R., Hämäläinen, A., Langenbuch, S., Danilin, S., Hádek, J., Hegyi, G., Kuchin, A., Panayotov, D., Validation of coupled neutron-kinetic / thermal-hydraulic codes Part 1: Analysis of a VVER-1000 transient (Balakovo-4), Annals of Nuclear Energy 28, 857–873 (2001)

[2]	Hämäläinen, A., Kyrki-Rajamäki, R., Mittag, S., Kliem, S., Weiss, F. P., Langenbuch, S., Danilin, S., Hádek, J., Hegyi, G., Validation of coupled neutron-kinetic / thermal-hydraulic codes Part 2: Analysis of a VVER-440 transient (Loviisa-1), Annals of Nuclear Energy 29, 215–321 (2002)

[3] 	ROHDE, U., LANGENBUCH, S., Gekoppelte Berechnungen von Thermohydraulik und Neutronenkinetk, Jahrestagung Kerntechnik, 18. - 20. Mai 1999, Karlsruhe, Sammelband "Neue Ergebnisse aus F+E zur Fluiddynamik und Reaktorphysik", Inforum Verlagsgesellschaft, Bonn, Juni 1999

[4]	CRISSUE-S – WP2 (Part 2 of REAC-SOAR), Neutronics / thermal-hydraulics coupling in LWR technology: STATE-OF-THE-ART REPORT, DIMNP NT 520(03), Pisa, December 2003

[5]	LANGENBUCH, S., LIZORKIN, M., ROHDE, U., VELKOV, K., 3D Neutronic Codes coupled with Thermo-Hydraulic System Codes for PWR, BWR and VVER Reactors, OECD/CSNI Workshop on Neutronic Codes Requirements, Annapolis, Md., USA, November 5-8, 1996, Proc. pp. 506-517

[6]	LANGENBUCH, S., Austregesilo, H., Fomitchenko, P., ROHDE, U., VELKOV, K., Interface Requirements to Couple Thermal-Hydraulic Codes to 3D Neutronic Codes, OECD/CSNI Workshop on Neutronic Codes Requirements, Annapolis, Md., USA, November 5-8, 1996, Proc. pp. 381-388

[7]	Weiss, F. P., Mittag, S., Validation of coupled neutron-kinetic / thermal-hydraulic codes against transients measured in VVER reactors, Phare SRR-1/95: Final Technical Report FZR/SRR195/FIN2.1, Brussels, Belgium (2000)

[8] 	TODOROVA, N., IVANOV, K., TAYLOR, B., Pressurized water reactor main steam line break benchmark, vol. 4: Results of Phase III on coupled Core-plant Transient Modelling, NEA-Report 3129, NEA/NSC/DOC(2003)21, Paris, France (2003)

[9]	NEA/CSNI: OECD/NRC Boiling Water Reactor Turbine Trip Benchmark, NEA/NSC/DOC/…, Final report to be published in Paris, France (2004)

[10]	IVANOV, B., IVANOV, K., GROUDEV, P., PAVLOVA, M., VVER-1000 Coolant Transient Benchmark, PHASE 1, vol. 1: Main Coolant Pump switching on - Final Specifications, NEA/NSC/DOC(2002)6, Paris, France (2002)

[11]	KLIEM, S., Danilin, S., Kyrki-Rajamäki, R., Hadek, J., Kereszturi, A., Siltanen, P., A Benchmark for Coupled 3D Neutron Kinetics/Thermohydraulics System Codes - Main Steam Header Break in a NPP with VVER-440 Reactor, Proc. Int. Conf. on Mathematics and Computation, Reactor Physics and Environmental Analysis in Nuclear Applications (1999), vol. 1, pp. 359-368, Senda Editorial, S.A., Madrid (Spain)

[12]	Kliem, S., Seidel, A., Comparison of the Results of the 6. Dynamic AER Benchmark - Main Steam Line Break in a NPP with VVER-440,
11. AER Symposium on VVER Reactor Physics and Reactor Safety, Csopak, Hungary, 2001, Proceedings pp. 295-329

[13]	KLIEM, S., Analysis and Calculation of an Accident with Delayed Scram at NPP Greifswald using the Coupled Code System DYN3D/ATHLET, Int. Conf. On the Physics of Nuclear Science and Technology, ANS, La Grange Park (Ill.), USA 1998, Proc. pp. 485-491

[14] 	LANGENBUCH, S., Status Report on Uncertainty and Sensitivity Methods, EU FP5 Report VALCO/WP2/D2, Brussels, Belgium (2002)

[15] 	Grundmann, U. and Hollstein, F., A Two-Dimensional Intranodal Flux Expansion Method for Hexagonal Geometry, Nucl. Sci. Eng. 133, 201-212 (1999)

[16] 	Grundmann, U., Rohde, U., and Mittag, S., DYN3D - Three Dimensional Core Model for Steady-State and Transient Analysis of Thermal Reactors, PHYSOR 2000, Pittsburgh, USA, (2000), Proceedings, ISBN 0-89448-655-1

[17] 	Kyrki-Rajamäki, R., Three-dimensional reactor dynamics code for VVER type nuclear reactors, Espoo: Technical Research Centre of Finland, VTT Publications 246, Dr. Tech. Thesis (1995)

[18] 	Keresztúri, A., Hegyi, Gy., Marázcy, Cs., Panka, I., Telbisz, M., Trosztel, I., and Hegedűs, Cs., Development and validation of the three-dimensional dynamic code KIKO3D. Annals of Nuclear Energy 30, 93-120 (2003)

[19] 	Lizorkin, M. P., Semenov, V. N., Ionov, V. S., Lebedev, V. I., Time Dependent Spatial Neutron Kinetic Algorithm for BIPR8 and its Verification, Second Symposium of AER, Paks, Hungary, 1992, Proceedings pp. 389-407

[20]	Teschendorff, V., Austregesilo, H., Lerchl, G., Methodology, Status and Plans for Development and Assessment of the Code ATHLET, OECD/CSNI Workshop on Transient Thermal-Hydraulic and Neutronic Codes Requirements, Annapolis, USA, 1996. Proceedings pp. 112-128

[21]	Miettinen, J., Hämäläinen, A., Development and Validation of the Fast Running Thermohydraulic Model SMABRE for Simulator Purposes, ICONE-8: International Conference on Nuclear Engineering, Baltimore, USA, 2000 [CD-ROM]. New York: American Society of Mechanical Engineers. Proceedings: Paper ICONE8-8188, p. 12

[22]	ALLISON, C.M., SCDAP/RELAP5/MOD3.1 Code Manual, INEEL, 1992

[23]	Strmensky, C., The continuing progress of RELAP5/DYN3D coupled code development, AER Working Group „D“ Meeting on VVER REACTOR SAFETY ANALYSIS, Moscow, Russia 2001

[24]	Grundmann, U., Lucas, D., Rohde, U., Coupling of the Thermohydraulic Code ATHLET with the Neutron Kinetic Core Model DYN3D, International Conference on Mathematics and Computations, Reactor Physics, and Environmental Analyses, Portland, USA, 1995. Proceedings p. 257

[25]	Hegyi, Gy., Kereszturi, A., Trosztel, I., Langenbuch, S., Horche, W., Velkov, K., Improvement of Plant Transient Analysis for VVER by Coupling KIKO3D with ATHLET, ICONE-6: International Conference on Nuclear Engineering, San Diego CA, USA, 1998. Proceedings of ICONE-6

[26]	Strmensky C., Darilek P., Hlbocky P., Suchon, M., Drop of control rod No. 287 in Unit 3 of NPP Bohunice, EU FP5 Report VALCO/WP1/EBO-VUJE-1, Brussels, Belgium (2002)

[27]	Siko, D., Strmensky, C., Outage of Three Main Coolant Pumps, (the 2nd Unit Of Mochovce NPP), EU FP5 Report VALCO/WP1/EMO-VUJE-2, Brussels, Belgium (2002)

[28]	Hádek, J. Macek, J.: Shut-down of 2 from 6 Working MCPs at 100 % Nnom in Dukovany NPP, EU FP5 Report VALCO/WP1/NRI-1, Brussels, Belgium (2002)

[29]	Stefanova, S., Stoyanov, K., Passage, G., Hristova, V., Atanasova, B., Stoimenova, D., Collection, Evaluation And Documentation Of Measured Data From Two Transients At The Kozloduy NPP 6th Unit Incommissioning (1st Fuel Cycle), EU FP5 Report VALCO/WP1/INRNE-1, Brussels, Belgium (2002)

[30]	Kuchin, A., Khalimonchuk, V., Several Single Control Rod Movements (Insertion/Withdrawn) at VVER-1000/V-320 of Rivne NPP, EU FP5 Report VALCO/WP1/SSTC-1, Brussels, Belgium (2002)

[31]	Hämäläinen, A., Kaloinen, E., Vanttola, T., VTT Calculations of the Bohunice Rod Drop Transient, EU FP5 Report VALCO/WP1/VTT-BO-CALC, Brussels, Belgium (2003)

[32]	Hegyi, G, Keresztúri, A., Trosztel, I, Aeki Calculations Of The Bohunice Rod Drop Transient, EU FP5 Report VALCO/WP1/AEKI-BO-CALC, Brussels, Belgium (2003)

[33]	Hádek. J., Lahovský, F., Macek. J., NRI Calculations of the Bohunice Rod Drop Transient, EU FP5 Report VALCO/WP1/NRI-BO-CALC-1, Brussels, Belgium (2003)

[34]	Strmensky, C., Darilék, P., Kvizda, B., Suchon, M., Hlbocky, P., VUJE Calculations Of The Bohunice Rod Drop Transient, EU FP5 Report VALCO/WP1/VUJE-BO-CALC, Brussels, Belgium (2003)

[35]	Danilin, S., Nikonov, S., Lizorkin, M., KI Calculations Of The Bohunice Rod Drop Transient, EU FP5 Report VALCO/WP1/KI-BO-CALC, Brussels, Belgium (2003)

[36]	Kliem, S., Kozmenkov, Y., Mittag, S., Weiss, F.-P., FZR Calculations of the Kozloduy MCP Switching off Transient, EU FP5 Report VALCO/WP1/FZR-KO-CALC, Brussels, Belgium (2003)

[37]	Hämäläinen, A., Kaloinen, E., Vanttola, T., VTT Calculations of the Kozloduy Pump Trip Transient, EU FP5 Report VALCO/WP1/VTT-KO-CALC, Brussels, Belgium (2003)

[38]	Kuchin, A., Khalimonchuk, V., SSTC NRS Calculations Of Coast-down of one of three working MCPs at Kozloduy, unit 6, EU FP5 Report VALCO/WP1/SSTC NRS-KOZ-CALC, Brussels, Belgium (2003)

[39]	Danilin, S., Nikonov, S., Lizorkin, M., KI Calculations of the Kozloduy Pump Trip Transient, EU FP5 Report VALCO/WP1/KI-KO-CALC, Brussels, Belgium (2003)

[40]	Stefanova, S., Passage, G., Hristova, V., Atanasova, I., Mandev, I., INRNE Calculations of the Kozloduy NPP, Unit 6, Main Coolant Pump Coast-down Transient (One of Three) during the Start-up Experiments, 1st Fuel Cycle, EU FP5 Report VALCO/WP1/INRNE-CALC-1, Brussels, Belgium (2003)

[41]	Guttman, I., Statistical Tolerance Regions: Classical and Bayesian. Griffin, London (1970)

[42]	Langenbuch, S., Krzykacz-Hausmann, B., Schmidt, K.-D., Hegyi, G., Keresztúri, A., Kliem, S., Hádek, J., DANILIN, S., Nikonov,. S., Kuchin, A., Khalimonchuk, V., Hämäläinen, A., Uncertainty and Sensitivity Analysis of two VVER Plant Transients in Loviisa-1 (VVER-440) and Balakovo-4 (VVER-1000), EU FP5 report VALCO/WP2/D10, Brussels, Belgium (2004)

[43]	Ionov, V. S., Kravchenko, Yu. Ya., Krainov, Yu. A., and Obuhov, V. K., Experimental Investigations of the VVER Physics on Critical Facilities in USSR, 1st Symposium of AER, Řež, Czech Republic, 1991, Proceedings, pp. 144-149

[44]	Ionov, V. S., Krainov, Yu. A., Epanechnikov, Yu. A., and Baryjbkin, V. I., Measurements at V-1000 Critical Facility: Kinetics Experiments Description, EU FP5 report VALCO/WP3/MEAS(D3)-2, Brussels, Belgium (2002)

[45]	Hutton, J.I., New Capabilities of the WIMS Code, PHYSOR 2000, Pittsburgh, USA, Proceedings, ISBN 0-89448-655-1

[46]	Edenius, M., Ekberg, K., Forssén, B.H., and Knott, D., CASMO-4, A Fuel Assembly Burnup Program, User’s Manual, STUDSVIK/SOA-95/1, Studsvik of America, Inc., USA 1995

[47]	Casal, J.J., Stammler, R.J.J., Villarino, E.A., and Ferri, A.A., HELIOS: Geometric Capabilities of a New Fuel Assembly Program. Intl. Topical Meeting on Advances in Mathematics, Computations and Reactor Physics, Pittsburgh, Pennsylvania, USA, 1991, Proceedings Vol. 2, p. 10.2.1-1

[48]	Sidorenko, V.D., Bolshagin, S.N., Lazarenko, A.P., Tomilov, M.Yu., Tsvetkov, V.M., Spectral Code TVS-M for Calculation of Characteristics of Cells, Supercells and Fuel Assemblies of VVER-Type Reactors, 5th Symposium of AER, Dobogoko, Hungary, 1995, Proceedings, pp. 121-130

[49]	Maiorov, L. (Ed.), Andrzejewski, K., Apostolov, T., Becker, R., Gado, J., Keresztúri, A., Laletin, N., Lebedev, V., Lelek, V., Lizorkin, M., Makai, M., Novikov, A., Pshenin, V., Yudkevich, M., Theoretical Investigations of the Physical Properties of WWER-type Uranium-Water Lattice (Final report of temporary international collective - TIC, Volume 2), Akadémiai Kiadó, Budapest, Hungary (1994) ISBN 963-05-6682-6

[50]	Petkov, P.T., Calculation of Accurate Albedo Boundary Conditions for Three-Dimensional Nodal Diffusion Codes by the Method of Characteristics, 10th Symposium of AER, Moscow, Russia, 2000. Proceedings, pp. 407-417

[51]	Petkov, P.T., Development of a Neutron Transport Code for Many-Group Two-Dimensional Heterogeneous Calculations by the Method of Characteristics, 10th Symposium of AER, Moscow, Russia, 2000. Proceedings, pp. 271-280

[52]	Mittag, S., Grundmann, U., Weiss, F.-P., Petkov P.T., Kaloinen, E., Keresztúri, A., Panka, I., Kuchin, A., Ionov, V. S., and Powney, D., Results of Validation Calculations Using Different Codes, EU FP5 Report VALCO/WP3/D11, Brussels, Belgium (2003)

[53]	Kuchin, A. and Khalimonchuk, V., SSTC Calculations for the V-1000 Facilty of the Kurchatov Institute, EU FP5 Report VALCO/WP3/D11-SSTCNRS, Brussels, Belgium (2003)

[54]	Suslov, A. A., Ionov, V. S., and Lizorkin, M. P., RRC KI Calculations for WP-3 Tasks, EU FP5 Report VALCO/WP3/D11-KI, Brussels, Belgium (2003)

[55]	Kaloinen, E., VTT Calculations for the V-1000 Facility of the Kurchatov Institute, EU FP5 Report VALCO/WP3/D11-VTT, Brussels, Belgium (2003)

[56]	Panka, I. and Keresztúri, A., KFKI-AEKI Calculations for the V-1000 Facility of the Kurchatov Institute, EU FP5 Report VALCO/WP3/D11-AEKI, Brussels, Belgium (2003)

[57]	Petkov, P.T., Helios/Mariko and Diffusion Calculations for the V-1000 and Comparison to Measurements, In: Minutes of the 2nd EU FP5 VALCO Project Meeting, Budapest, Hungary (2002)

[58]	Petkov, P.T., Calculation of Radial Boundary Conditions for the V-1000 Facility, In: Minutes of the 3rd EU FP5 VALCO Project Meeting, Garching, Germany (2003)

[59]	Powney, D., Input Data for V-1000 Calculations: Macroscopic Cross-Section Library by WIMS, EU FP5 Report VALCO/WP3/WIMSDAT-1(D5), Brussels, Belgium (2002)

[60]	Hádek, J. and Grundmann, U., Reconstruction of Point-wise Neutron Flux Distribution in a Hexagonal Cassette, 7th Symposium of AER, Zittau, Germany, 1997, Proceedings, pp. 470-486

[61]	Mittag, S., Petkov, P.T., and Grundmann U., Discontinuity factors for non-multiplying material in two-dimensional hexagonal reactor geometry, Annals of Nuclear Energy 30, 1347–1364 (2003)

[62]	F. MENTER, ECORA: CFD Best Practice Guidelines for CFD Code Validation for Reactor-Safety Applications, EU FP5 Report EVOL-ECORA-D01, Brussels, Belgium (2002)

# TABLES

Table I: Participants, used coupled codes and calculated cases

| parti-cipant | Country | Coupled code: | VVER-440 Bohunice | VVER-1000 Kozloduy |
| --- | --- | --- | --- | --- |
| FZR | Germany | ATHLET-DYN3D |  | + |
| VTT | Finland | HEXTRAN-SMABRE | + | + |
| KFKI | Hungary | ATHLET-KIKO3D | + |  |
| NRI | Czech Republic | ATHLET-DYN3D | + |  |
| INRNE | Bulgaria | ATHLET-DYN3D |  | + |
| VUJE | Slovakia | RELAP5-DYN3D | + |  |
| SSTC NRS | Ukraine | ATHLET-DYN3D |  | + |
| KI | Russia | ATHLET-BIPR-8 | + | + |

Table II: Event sequence of the Loviisa transient ‘Load drop of one turbo-generator at nominal power’

| Nr | Time | Event | Consequences |
| --- | --- | --- | --- |
| 1 | 0 s | Load drop of one turbo-generator | Pressure increase on secondary side |
| 2 | 0 – 100 s | Step-wise insertion of control rod group 6 | Reduction of neutron power from nominal to about 60 % with an intermediate hold at 50 s |
| 3 | 20 – 100 s | After the increase of primary pressure the pressure control system activates heater switch-off and pressurizer spray valve opening | These actions lead to a decrease of primary pressure |
| 4 | 20 – 100 s | Actions of volume control system by letdown opening | These actions lead to a decrease of water level in pressurizer |
| 5 | 100 s | After the decrease of primary pressure the heaters of pressurizer are activated by the pressure control system | Increase of pressure, this is also affected by volume control means |
| 6 | 100 s | Actions of volume control system by make-up injection | Increase of water level, which also contributes to increase of pressure |

Table III: Relevant physical phenomena of the Loviisa-1 transient

| Nr | Reference to Table II | Time-period | Event or Physical phenomena | Affected parameters |
| --- | --- | --- | --- | --- |
| 1 | 1 | 0 -20 s | Load drop of one turbo-generator | Pressure increase on secondary side |
| 2 |  | 0 -20 s | Reduction of heat transfer between primary and secondary side | Increase of primary pressure Increase of cold leg temperatures |
| 3 |  | 0 - 20 s | Heat-up of primary circuit and volume expansion of primary coolant | Increase of primary pressure and activation of pressure control in the pressurizer |
| 4 | 2 | 0 – 100 s | Step-wise Insertion of control rod group 6 leading to a power reduction | Reduction of nuclear power generation and consequently decrease of coolant temperatures and decrease of water level |
| 5 | 3 | 20 – 100 s | Pressure control in the pressurizer to reduce the pressure ( energy balance and condensation) | Primary pressure and water level in the pressurizer |
| 6 |  | 100 – 700 s | Long term pressure control in the pressurizer to increase and stabilize the pressure | Primary pressure and water level in the pressurizer |

Table IV: List of uncertain factors or uncertain model parameters of transient analysis

| Nr | Reference to Table III | Models or parameters |
| --- | --- | --- |
| 1 | 1 | Time point of load drop is fixed |
| 2 | 2 | Time function of secondary pressure. In ATHLET this time function is generated by a GCSM model using feed water flow and steam extraction to obtain good agreement with measured values. What time functions are acceptable in comparison to measurement? Compare time functions of ATHLET and SMABRE. What affects the heat-transfer from primary to secondary side? Water level, nodalization other model parameters (HTC)? |
| 3 | 3 | Heat-transfer from primary to secondary side Volume of primary circuit Total mass flow (value and time function) Primary pressure control |
| 4 | 4 | What are reasonable control rod insertion programmes that are acceptable with measurement? Which models were already used by participants (FZR)? |
| 5 | 5 | Pressure control system (time-point of switching-off heaters, efficiency of spray system) Volume control system (time-point of letdown opening, capacity of letdown system, duration of operating letdown system) |
| 6 | 6 | Time of starting make-up system, capacity of make-up system. What variants of make-up flow are reasonable? Time of operating heaters |

Table V: List of uncertain parameters for Loviisa-1 transient with range of parameter values and their probability distributions

| No. | Parameter description and distribution(s) |
| --- | --- |
| 1 | Function of secondary pressure: correction factor (convex mixture), GRS, FZR, NRI, AEKI: Uniform [-0.1, 1.1], VTT: Histogram [0.0, 0.1, 300.0, 320.0, 0.08, 0.84, 0.08] |
| 2 | Model for control rod insertion (1=variant A as SMABRE, 2=variant B as FZR for base case), Discrete [1 2 / 0.5, 0.5] |
| 3 | Total reactivity worth of control rod group: correction factor - GRS, FZR, VTT: Triangular [0.8, 1.0, 1.1], NRI, AEKI: Uniform [0.8, 1.1] |
| 4 | Shape of axial burn-up distribution: correction factor (not used by GRS) - Uniform [0.8, 1.0] |
| 5 | Mass flow rate [kg/s] between upper head and upper plenum - Uniform [10.0, 300.0] |
| 6 | Operation of make-up system: time lag of the start of the 2nd pump [s] – GRS, FZR, VTT: Triangular [20.0, 40.0, 200.0], NRI, AEKI: Uniform [20.0, 200.0] |
| 7 | Heaters in PRZ: heat-up time-constant [s] - Uniform [2.0, 15.0] |
| 8 | Heaters in PRZ: total heating power, correction factor - Uniform [0.8, 1.0] |
| 9 | Fuel rod gap heat transfer coefficient [W/m²K] - GRS, FZR: Uniform [3000, 12000], VTT: Uniform [0.64, 1.98], NRI, AEKI: Polygon [3000, 5000, 10000, 12000 / 0, 1, 1, 0] |
| 10 | Core bypass [%] - Uniform [3.0, 12.0] |
| 11 | correction factor for DCDOPP (not used by GRS and VTT) - FZR: Uniform [0.8, 1.2], NRI, AEKI: Triangular [0.8, 1.0, 1.2] |
| 12 | correction factor for DCRHO (not used by GRS and VTT) - FZR: Uniform [0.8, 1.2], NRI, AEKI: Triangular [0.8, 1.0, 1.2] |

Table VI: List of working groups and their simulation codes for Loviisa-1 transient

| GRS | ATHLET with point kinetics |
| --- | --- |
| FZR | ATHLET – DYN3D |
| NRI | ATHLET – DYN3D |
| AEKI | ATHLET – KIKO3D |
| VTT | SMABRE - HEXTRAN |

Table VII: Event sequence of the Balakovo-4 transient, Switch-off of one of two steam generator feed water pumps

| Nr | Time | Event | Consequences |
| --- | --- | --- | --- |
| 1 | 0 s | Switch-off of one feed water pump | Pressure increase on secondary side in main steam header |
| 2 | 2 - 6 s | Drop of control rod group K1 within 4 s | Reduction of neutron power from nominal to about 63 % |
| 3 | 10 – 50 s | Insertion of control rod group K10 with 2 cm/s | Reduction of neutron power to about 50 % |
| 4 | 50 – 200 s | Further insertion of control rod group K10 by power control | Further reduction of neutron power to about 45 % |
| 5 | 300 – 700 s | The pressure on secondary side is stabilized at 6.0 MPa by the controller | Pressure on secondary side stabilized at 6.0 MPa |

Table VIII: Relevant physical phenomena of the Balakovo-4 transient

| Nr | Reference to Table VII | Time-period | Event or Physical phenomena | Affected parameters |
| --- | --- | --- | --- | --- |
| 1 | 1 | 0 -50 s | Reduction of feed water due to switch-off of one feed water pump | Pressure increase on secondary side |
| 2 | 2 | 0 -6 s | Reduction of neutron power generation due to drop of control rod group K1 | Decrease of neutron power Decrease of upper plenum pressure as well as of coolant temperatures in hot and cold legs |
| 3 | 3 | 0 - 200 s | Further reduction of power by insertion of control rod group K10 | Decrease of power to 45 % establishing new stable plant conditions |
| 4 |  | 200 – 700 s | Stabilizing plant conditions by pressure control on primary and secondary side | Nearly steady state conditions for neutron power and coolant temperature, continuous increase of primary pressure |

Table IX: List of uncertain parameters for Balakovo-4 transient with range of parameter values and their probability distributions

| No. | Parameter description and distribution(s) |
| --- | --- |
| 1 | Function of secondary pressure: correction factor - Uniform [-0.1, 1.1] |
| 2 | Total reactivity worth of control rod group K1 - Triangular [0.7, 1.0, 1.1] |
| 3 | Total reactivity worth of control rod group K10 - Triangular [0.7, 1.0, 1.1] |
| 4 | Shape of axial burn-up distribution: correction factor (not used by GRS) -Uniform [0.8, 1.0] |
| 5 | Fuel temperature feedback - Discrete [1 2 3 each 1/3] |
| 6 | Moderator density feedback - Discrete [1 2 3 each 1/3] |
| 7 | Heaters in PRZ: heat-up time-constant [s] - Uniform [2.0, 20.0] |
| 8 | Heaters in PRZ: protection influence factor - Discrete [1 2 each 0.5] |
| 9 | Fuel rod gap heat transfer coefficient [W/m²K] - Uniform [3000, 5000] |
| 10 | Mass flow of the feed water (not used by KI) - Uniform [0.9, 1.1] |
| 11 | Enthalpy of the feed water (not used by KI) - Uniform [0.9, 1.1] |

Table X: List of working groups and their simulation codes for Balakovo-4 transient

| GRS | ATHLET with point kinetics |
| --- | --- |
| FZR | ATHLET – DYN3D |
| SSTCNRS | ATHLET – DYN3D |
| KI | ATHLET – BIPR8 |

Table XI: Main operation data in four V-1000 steady states

| State- No. | Fuel and moderator temperature (oC) | Moderator boric acid concentration (g/l) | Moderator level*) (cm) | Control rod position | Short fuel rods |
| --- | --- | --- | --- | --- | --- |
| 1 | 15.2 | 8.49 | 253.5 | Group 10 fully inserted | present |
| 2 | 15.2 | 8.68 | 266.8 | All groups fully out | present |
| 3 | 18.6 | 8.74 | 324.0 | All groups fully out | not present |
| 4 | 14.0 | 8.80 | 325.0 | All groups fully out | not present |

*) distance from the fuel bottom

Table XII: Deviations of node-averaged powers calculated by different codes from measured values for the state with all control rods out of core

| Codes | HEXTRAN HELIOS (VTT) | KIKO3D HELIOS (AEKI) | DYN3D HELIOS (FZR) | BIPR-8 HELIOS (KI) | DYN3D NESSEL (SSTCNRS) |
| --- | --- | --- | --- | --- | --- |
| RMS error (%) | 4.9 | 5.1 | 5.0 | 6.8 | 5.5 |
| Max. Dev. (%) | 18.4 | 14.4 | 17.8 | 18.5 | 14.8 |

Table XIII: Deviations of node-averaged powers calculated by HEXTRAN (VTT) using different FA two-group data (all control rods out of core)

| Codes | HEXTRAN WIMS | HEXTRAN HELIOS | HEXTRAN CASMO |
| --- | --- | --- | --- |
| RMS error (%) | 4.5 | 4.9 | 5.1 |
| Max. Dev. (%) | 16.5 | 18.4 | 16.9 |

# FIGURES

Figure 1: The calculated relative radial power profile (Pfinal/Pinitial) in the indicated assembly row crossing the dropped rod position and one corresponding total core map (NRI calculation), Bohunice transient.

Figure 2: Calculated and measured fuel assembly outlet temperature in position next but one to the dropped rod, Bohunice transient.

Figure 3: Calculated and measured neutron power, Kozloduy transient.

Figure 4: Calculated and measured pressure increase in MCPs in loop 1 (pump trip, flow reverses), loop 3 (pump off, reversed flow from the beginning) and average of loops 2 and 4 (pumps running), Kozloduy transient.

Figure 5: Relative core power (GRS).

Figure 6: Relative core power (VTT).

Figure 7: RCC - Relative core power (GRS).

Figure 8: RCC - Relative core power (VTT).

Figure 9: Tolerance limits - Relative core power (GRS).

Figure 10: Tolerance limits - Relative core power (VTT).

Figure 11: Power distribution measured in the steady state with all control rods driven out of core, the line indicating a tilt.

Figure 12: Deviations (%) of node-averaged powers (calculated by different codes) from measured values for the state with all control rods driven out.

Rod insertion

16 ...  96 s

Rod withdrawal

800 … 837 s

Figure 13: Comparison of relative powers in FA 71 (next neighbour but three to the FA with the inserted CR), detector at the height of 285 cm. HELIOS data applied in all calculations.

Figure 14: Scram. Relative powers at detector position 126 L. HELIOS data applied.

Complete insertion of

cluster 126: 282 ...  317 s

Rod drop

65.5 ...  69.5 s