PAGE  

REVISITING CRITICAL ISSUES IN NUCLEAR REACTOR DESIGN/SAFETY BY USING

3D NEUTRONICS/THERMAL-HYDRAULICSS MODELS: STATE OF THE  ART REPORT
(CRISSUE-S)

CO-ORDINATOR
Prof. F. D’Auria
University of Pisa - DIMNP
Via Diotisalvi 2,
I - 56100 Pisa
ITALY
Tel.:
+ 39 050 836653
Fax:
+ 39 050 836665
LIST OF PARTNERS
1. ANAV-UPC, Barcelona, Spain

2. Studsvik Eco & Safety AB (later Studsvik Nuclear AB), Nykoping, Sweden

3. SKI, Sockholm, Sweden

4. University of Madrid, Madrid, Spain

5. University of Valencia, Valencia, Spain

6. NRI, Rez, Czech Republic

7. Pennsylvania State University, College Park, USA

8. University of Illinois at Urbana-Champaign, Urbana, USA

9. OECD/NEA, Paris, France

10. FZR (VALCO Project Coordinator), Rossendorf, Germany

11. Royal Institute of Technology, Stockholm, Sweden

12. Westinghouse Atom AB, Vasteras, Sweden

CONTRACT N°:
FIKS-CT-2001-00185
EC Contribution:






EUR 150.000

Total Project Value:






EUR 270.000

Starting Date:







January 1st, 2002

Duration:







24 months

CONTENTS
LIST OF ABBREVIATIONS AND SYMBOLS
EXECUTIVE SUMMARY
A.
OBJECTIVES AND SCOPE
B.
WORK PROGRAMME
B.1
Neutron Kinetics / Thermal-Hydraulics Coupling in LWR Technology: Data Requirements and Databases Needed for Transient Simulations and Qualification


B.2
Neutron Kinetics / Thermal-Hydraulics Coupling in LWR Technology: State-Of-The-Art Report



B.3
Neutron kinetics / Thermal-Hydraulics Coupling in LWR Technology: Achievements and Recommendations Report
C.
WORK PERFORMED AND RESULTS


C.1
Introductory Remarks


C.2
Transients to be considered by Coupled Analyses


C.3
Thresholds of Acceptability for Coupled Codes Results


C.4         The Role of Fuel


C.5

The Best-Estimate Approach






C.5.1 Methodology   



C.5.2 Uncertainties 

C.5.3 Sources of Uncertainty

C.5.3.1 Fuel related

C.5.3.2.Related to other phenomena or components

C.5.3.3 Related to models and codes

        C.6 
Needed Data Base and Suitable Codes

        C.7  
Created Data Base and Transient Analysis Results

   C.7.1 Transients Suitable For Validation

   C.7.2 Results from available calculations

C.8 

Qualification Requirements






C.8.1 Suitable Level of Detail for Input Deck
C.8.2 Qualification of TH Nodalisations and Codes

C.8.3 Qualification of Neutron-Kinetics Nodalisations and Codes

C.8.4 Coupling Qualification



C.9 

Licensing Status



C.10

Use by Industry

CONCLUSION
REFERENCES
TABLES
LIST OF  ABBREVIATIONS AND SYMBOLS * 

	ABB
	= Asea Brown Boveri

	ABWR
	= Advanced Boiling Water Reactor

	ACC
	= Accumulator

	ACMFD
	= Analytical Coarse Mesh Finite Difference Method

	ADF
	= Assembly Discontinuity Factor

	AEC
	= see US AEC

	AFENM
	= Analytical Function Expansion Nodal Method

	AGCR
	= Advanced Gas Cooled Reactors 

	AGR
	= Advanced Gas Reactor

	AHTLM
	= Adaptive High-order Table Lookup Method

	ANAV-UPC
	= Asociación Nuclear Ascó-Vandellòs, Technical University of Catalonia

	ANM
	= Analytic Nodal Method

	ANS
	= American Nuclear Society

	AOA
	= Axial Offset Asymmetry (Guidelines)

	APA
	= Advanced Plutonium Assembly

	APRM
	= Average Power Range Monitor

	AP-1000
	= Advanced PWR (1000 MWe)

	ASME
	= American Society of Mechanical Engineering

	ASTM
	= American Society of Testing and Materials

	ATHLET
	= Analysis of THermal-hydraulics of LEaks 

	ATWS
	= Anticipated Transient Without Scram

	AZ
	= (Russian acronym for scram)

	BDBA
	= Beyond Design Basis Accident

	BE
	= Best-Estimate

	BFSB
	= BWR Full Size Bundle Test

	BiLU
	= Blockwise incomplete, or Biconjugated Lower Upper (numerics pre-conditioner)

	BOA
	= Boron induced Offset Anomaly

	BOC
	= Beginning of (fuel) Cycle (into the reactor core)

	BOP
	= Balance of Plant

	BP
	= Burnable Poison

	BPLU
	= Border Profiled Lower Upper matrix solver (numerical method)

	BU
	= Burn-up

	BWR
	= Boiling Water Reactor

	BWRS
	= BWR Stability

	BWRTT
	= Boiling Water Reactor Turbine Trip, see also TT

	B&W
	= Babcock & Wilcox

	CAEC
	= Czechoslovak Atomic Energy Commission

	CANDU
	= Canadian Deuterium Uranium

	CDF
	= Corner Discontinuity Factor

	CEA
	= Commissariat a l’Energie Atomique

	CERCER
	= CERamic matrix and CERamic fuel

	CERMET
	= CERamic fuel and METallic matrix

	CFD
	= Computational Fluid-Dynamics

	CFR
	= Code of Federal Regulation (of US NRC)

	CHF
	= Critical Heat Flux

	CIAU
	= Code with capability of Internal Assessment of Uncertainty

	CILC
	= Crud Induced Localized Corrosion

	CL
	= Cold Leg

	CMF
	= Common Mode Failure

	CMFD
	= Coarse Mesh Finite Difference

	CPM
	= Collision Probability Method

	CPU
	= Central Process Unit

	CR
	= Control Rod

	CRGT
	= Control Rod Guide Tubes

	CRHFT
	= Core Region at High (centre-line) Fuel Temperature

	CRHST
	= Core Region at High (fuel rod) Surface Temperature

	CRP
	= Coordinated Research Project

	CRISSUE-S
	= Critical Issues in Nuclear Reactor Technology: a State of The Art Report

	CSAU
	= Code Scaling, Applicability and Uncertainty (US NRC uncertainty method)

	CSC
	= Cross Section Code

	CSNI
	= Committee on the Safety of Nuclear Installations

	CT
	= Coolant Transient

	CVCS
	= Chemical and Volume Control System

	DBA
	= Design Basis Accident

	DC
	= Downcomer (of RPV)

	DEC
	= Département d’études des Combustibles (CEA - Cadarache)

	DF
	= Discontinuity Factor

	DNB
	= Departure from Nucleate Boiling

	DNBR
	= DNB Ratio

	DO
	= Dry-out

	DOE
	= Department of Energy (of US)

	DR
	= Decay Ratio

	DUPIC
	= Direct Use of Spent PWR Fuel in CANDU reactors

	DW
	= Density Wave (originated)

	EBA
	= Enriched Boron Addition

	ECCS
	= Emergency Core Cooling System

	ENAC
	= European Nuclear Assistance Consortium 

	EOC
	= End of Cycle

	EOP
	= Emergency Operating Procedure

	EP
	= External (recirculation) Pump (BWR)

	EPMA
	= Electron Probe Micro Analysis

	EPRI
	= Electric Power Research Institute

	ES
	= Eigenvalue Separation

	ESFAS
	= Engineered Safety Features Actuation System

	EU
	= European Union

	FA
	= Fuel Assembly

	FEBE
	= Forward-Euler, Backward-Euler (Athlet module)

	FGR
	= Fission Gas Release

	FMS
	= Fuel Management System 

	FSAR
	= Final Safety Analysis Report

	FP
	= Full Power or Fission Product

	FR
	= Fast (Neutron) Reactor

	FTC
	= Fuel Temperature Coefficient

	FW
	= Feed-Water

	FWHM
	= Full Width (of the concerned peak) at Half Maximum

	FZR
	= Forschungszentrum Rossendorf (near Dresden, Germany)

	GCSM
	= Transients General Control Simulation Module (Athlet module)

	GE
	= General Electrics

	GI
	= General Interface

	GMRES
	= A generalised minimal residual algorithm 

	GRS
	= Gesellschaft fuer Anlagen- und Reaktorsicherheit (also ID for uncertainty method)

	HCO
	= Heat Conduction Objects (of Athlet)

	HECU
	= Heat Transfer and Heat Conduction (Athlet module)

	HFP
	= Hot Full Power

	HL
	= Hot Leg

	HOSG
	= Horizontal (Tubes) Steam Generator

	HPIS
	= High Pressure Injection System

	HPLWR
	= High Performance LWR

	HT
	= Heat Transfer

	HTA
	= Heat Transfer Area

	HTC
	= Heat Transfer Coefficient

	HTGR
	= High Temperature Gas Reactor

	HTR
	= High Temperature Reactor

	HWR
	= Heavy Water Reactor

	HZP
	= Hot Zero Power

	IAEA
	= International Atomic Energy Agency

	IASCC
	= Irradiation Assisted Stress Corrosion Cracking

	ICE
	= (numerical solution method)

	ID
	= Identification

	IET
	= Integral Effect Test (Facility)

	IFPE
	= International Fuel Performance Experiment

	IGSCC
	= Intergranular Stress Corrosion Cracking

	IMF
	= Inert‑Matrix Fuel

	IP
	= Internal (recirculation) Pump (BWR)

	IRI
	= Interfaculty Reactor Institute - Delft University - The Netherlands

	ITF
	= Integral Test Facility

	IWGATWR
	= IAEA Int. Working Group on Advanced Technologies for Water Cooled Reactors

	JP
	= Jet Pump (BWR)

	KAERI
	= Korean Atomic Energy Research Institute

	KKL
	= Leibstadt NPP

	KTH
	= Kungl. Tekniska Högskolan

	KWU
	= KraftWerk Union

	LBLOCA
	= Large Break Loss of Coolant Accident

	LMFR
	= Liquid Metal Fast Reactor

	LOCA
	= Loss of Coolant Accident

	LOFW
	= Loss of Feed-water

	LOOP
	= Loss Of Off-site Power

	LPRM
	= Local Power Range Monitor

	LPIS
	= Low Pressure Injection System

	LWR
	= Light Water Reactor

	MCP
	= Main Coolant Pump

	MFT
	= Maximum Fuel (Centerline) Temperature

	MIT
	= Massachusetts Institute of Technology

	MLIV
	= Main Loop Isolation Valves

	MOX
	= Mixed U-Pu oxide nuclear fuel

	MPI
	= Multi-Processor Interaction

	MSIV
	= Main Steam Isolation Valve

	MSLB
	= Main Steam Line Break

	MTU
	= Metric tons of Uranium

	MWD
	= Megawatt-Day

	NACUSP
	= NAtural cirCUlation and Stability Performance of BWRs

	NC
	= Natural Circulation

	NCM
	= The Nodal Collocation Method

	NCTH
	= Nuclear Coupled Thermal-Hydraulics

	NEA
	= Nuclear Energy Agency

	NEM
	= Nodal Expansion Method

	NEUKIN
	= Neutron Kinetics (Athlet module)

	NK
	= Neutron Kinetics

	NKC
	= Neutron Kinetics Code

	NMCA
	= Noble Metal Chemical Application, or Noble Metal Clad Assembly

	NPP
	= Nuclear Power Plant

	NRC
	= Nuclear Regulatory Commission (of US)

	NRI
	= Nuclear Research Institute (Czech Republic)

	NSC
	= Nuclear Science Committee

	NUGG
	= Natural uranium gas-graphite

	NUPEC
	= Nuclear Power Engineering Test Center

	OECD
	= Organization for Economic Co-operation and Development

	ODE
	= Ordinary Differential Equations

	O'M
	= Oxygen-to-Metal (ratio).

	ORNL
	= Oak Ridge National Laboratory

	OTSG
	= Once-Through Steam Generator

	PAMS
	= Post-Accident Monitoring System

	PBMR
	= Pebble Bed Modular Reactor

	PCCI
	= Pellet-cladding Chemical Interaction

	PCI
	= Pellet Clad Interaction

	PCMI
	= Pellet Clad Mechanical Interaction

	PCT
	= Peak Cladding Temperature

	PDE
	= Partial Differential Equations

	PEN
	= Polynomial Expansion Nodal (method)

	PF
	= Peak Factors (for linear power of fuel pins)

	PHWR
	= Pressurized HWR

	PIE
	= Post Irradiation Examination

	PORV
	= Pilot Operated Relief Valve

	PRZ
	= Pressurizer

	PRPS
	= Primary Reactor Protection System

	PSA
	= Probabilistic Safety Assessment

	PSU
	= Pennsylvania State University

	PVM
	= Parallel Virtual Machine

	PWR
	= Pressurized Water Reactor

	PZ-1
	= First protection level (Russian acronym)

	PZ-2
	= Second protection level (Russian acronym)

	QA
	= Quality Assessment

	QC
	= Quality Control

	RBMK
	= Boiling Water Cooled – Graphite Moderated (Russian Reactor)

	RCCA
	= Rod Cluster Control Assembly

	RCS
	= Reactor Coolant System

	REA
	= Rod Expulsion Accident

	REAC
	= Reactivity Accidents (ATWS, RIA, BWRS, Boron-dilution, Low Power)

	RFP
	= Robust Fuel Program (EPRI)

	RG
	= Regulatory Guide

	RHS
	= Right Hand Side

	RIA
	= Reactivity Initiated (or Induced) Accident

	RIT
	= Royal Institute of Technology (see also KTH)

	RPS
	= Reactor Protection System

	RPV
	= Reactor Pressure Vessel

	RSK
	= (German licensing guidelines)

	R&D
	= Research and Development

	SAPR
	= Semi-Analytical Perturbation Reconstruction (numerical module)

	SAR
	= Safety Analysis Report

	SBLOCA
	= Small Break Loss of Coolant Accident

	SCC
	= Stress Corrosion Cracking

	SEGFSM
	= ‘Special Experts’ Group on Fuel Safety Margins

	SET
	= Separate Effect Test (Facility)

	SG
	= Steam Generator

	SGTR
	= Steam Generator Tube Rupture

	SI
	= Safety Injection

	SIT
	= Safety Injection Tanks (used as synonymous of ACC) 

	SKI
	= Statens Kärnkraftinspektion (Swedish Nuclear Power Inspectorate)

	SL
	= Steam Line

	SOAR
	= State of the Art Report

	SONS
	= State Office for Nuclear Safety (Czech Republic)

	SOR
	= Successive Overrelaxation (numerical method)

	SPDS
	= Safety Parameter Display System

	SRV
	= Steam Relief Valve

	STP
	= Standard Temperature and Pressure

	SYS-TH
	= System Thermal-hydraulics

	TAMU
	= Texas A&M University

	TECDOC
	= Technical Document (issued by IAEA)

	TD
	= Thoria-based fuels

	TFD 
	= Thermo-fluid-dynamics (Athlet module)

	TFO
	= Thermo-Fluid-dynamic Object (of Athlet)

	T-H or T/H
	= Thermal-Hydraulics

	THSC
	= Thermal-Hydraulics System Code

	TIN
	= Transverse Integrated Nodal

	TIP
	= Traversing In-core Probe

	TMI-1
	= Three Miles Island (Unit 1)

	TPEN
	= Triangle-based Polynomial Expansion Method 

	TT
	= Turbine Trip (in BWR)

	TTEF
	= Total Thermal Energy released to the Fluid (during the calculated transient)

	UMAE
	= Uncertainty Method based on Accuracy Extrapolation

	UP
	= Upper Plenum

	UPISA
	= University of Pisa

	UPTF
	= Upper Plenum Test Facility

	URB
	= Accelerated off-loading of the unit (Russian acronym)

	UT
	= Ultrasonic (cleaning) Technology

	UTSG
	= U-Tubes Steam Generator

	US
	= See USA

	USA
	= United States of America

	US AEC
	= US Atomic Energy Commission

	UVA
	= University of Valencia

	VALCO
	= Validation of Coupled neutronics / thermal hydraulics codes for WWER reactors

	VUJE
	= Nuclear Power Plant Research Institute (Trnava, Slovak Republic)

	VVER
	= See WWER

	WANO
	= World Association of Nuclear Operators

	WESE
	= Westinghouse Energy Systems Europe

	WG
	= Weapon Grade

	WWER
	= Water-cooled Water-moderated Energy Reactor

	XRF
	= X-ray Fluorescence

	XS
	= Xenon Samarium

	0D or 0-D
	= Zero-Dimensional (point model)

	1D or 1-D
	= One-Dimensional

	2D or 2-D
	= Two-Dimensional

	3D or 3-D
	= Three-Dimensional


* Adopted in the entire set of CRISSUE-S reports

EXECUTIVE SUMMARY

The CRISSUE-S project aims at re-evaluating  fundamental technical issues in the technology of light water nuclear reactors that is connected with the interactions between neutron kinetics and thermal-hydraulics modeling aspects that deal with the neutron moderation and cause concerns for the accident performance of the NPP. All of this is done in the light of the advanced computational tools that are available to the scientific community.  

The objectives for the CRISSUE-S project are:

· Establishing a State-Of-the-Art (SOAR) on the subject. 
· Providing results of best estimate analyses of complex transients for existing NPP. 
· Providing recommendations to interested organizations.
· Identifying areas of the NPP design where the design/safety requirements can be relaxed.

The SOAR summarizes among other things the findings from recent international Projects or activities (e.g. OECD/CSNI SOAR on BWR, IAEA Workshops and TECDOC, OECD/NEA/NSC recent Benchmarks including the PWR-MSLB and the BWR-TT benchmarks, boiling stability activities in the EU IV Framework, etc.). Within this context, the results of a cooperation established with the EU VALCO project are discussed and consideration is given to the activities in progress within the EU NACUSP project. Parts of the SOAR on "Reactivity Accidents" (REAC) are: the selection of relevant transients from proper PSA studies; consideration of the needed tools and databases including computer codes; NPP nodalisations (input decks) and realistic boundary and initial conditions; consideration of criteria for using the mentioned tools and databases including the qualification process and the uncertainty evaluation. The establishment of a SOAR on REAC implies the availability of information about the system performance should relevant selected accident occur. Therefore, NPP transients have been analyzed and relevant results have been considered in the SOAR together with qualified results available from different sources. The accident scenarios are typically identified as MSLB, ATWS, LOFW, CR ejection, DW stability, MSIV closure and TT. Relevance of 3-D neutron  kinetics thermal-hydraulics coupling upon the prediction of a LBLOCA scenario is also evaluated. In relation to the mentioned transients, a ‘CRISSUE-S database’ has been created.  An answer is given to the following questions: “Will the assigned NPP core survive the assigned transient whatever the fuel type and the burn-up are?” If yes, what are the available safety margins? 

Main conclusions have been derived in relation to:

· Capabilities of 3D thermal-hydraulic computational tools. 
· List of transients in relation to which  coupled analyses are recommended (e.g. MSLB, LOFW-ATWS). 
· Identification of thresholds of acceptability: (e.g. for pressure pulses characterized by FWHM < 0.1 s acceptable error is 10 % nominal pressure).
· Relevance of the role of fuel. 
· Uncertainty.

· Licensing status. 
· Creation of a database of results from relevant coupled calculations. 
A. 
OBJECTIVES AND SCOPE

The controlled fission power has been utilized for electricity production worldwide for several decades in Nuclear Power Plants (NPP) based on Light Water Reactor (LWR) technology. It has proven its efficiency and safety during these years and has manifested itself to be a reliable and durable energy source. The foundation pillar in the peaceful utilization of the fission nuclear power has always been the strong emphasis on safety. The safety has been accomplished by continuously pursuing in depth reviews and re-evaluation of safety related issues incorporating findings from the worldwide continuously ongoing nuclear safety research activities. Specific requirements have been deployed at the design and in the permissible operation conditions of the NPP in order to always ensure adequate margins against critical system conditions, thus preventing accidents to occur. It is realized that as new findings and new analysis capabilities are available the safety will be increased and it is likely that also the applied safety margins can be relieved (decreased) without compromising the actual safety. Prevention and mitigation measures, however, must be properly balanced with cost reduction needs. A thorough knowledge of fundamental issues – in the present case the interaction between neutron kinetics and thermal‑hydraulics – allows pursuing the goal of ensuring safety at reasonable costs.

In line with this, the CRISSUE-S project was created with the aim of re-evaluating fundamental technical issues in the technology of LWR. Specifically, the project seeks to address the interactions between neutron kinetics and thermal-hydraulics that affect neutron moderation and influence the accident performance of the NPP. This is undertaken in the light of the advanced computational tools that are readily available to the scientific community today.

Specifically the CRISSUE-S activity deals with the control of fission power and the use of high burn-up fuel; these topics are part of the EC Work Programme as well as that of other international organizations such as the OECD/NEA and the IAEA. The problem of evaluating reactivity-induced accident (RIA) consequences and eventually deciding the possibility of NPP prolongation must be addressed and solved. RIA constitutes one of the most important of the ”less-resolved” safety issues, and resolution of this problem may have huge positive financial, social and environmental impact. Public acceptance of the nuclear technology implies that problems such as these be satisfactorily resolved.

The cross-disciplinary (regulators, industry, utilities and research bodies) interaction and co‑operation within CRISSUE-S provides results which can directly and immediately be beneficial to the EU industry. Co-operation at an international level; the participation of the EU, former Eastern European countries, the USA, and observers from Japan testify to the broad interest these problems engender. Competencies in broad areas such as thermal-hydraulics, neutron kinetics and fuel, overall system design and reactor surveillance are needed to address the problem that are posed here. Excellent expertise is available in specific areas, while limited knowledge exists in the interface zones of those areas, e.g. in the coupling between thermal-hydraulics and neutron kinetics. In general terms, the activities carried out and described here aim at exploiting available expertise and findings and gathering together expert scientists from various areas relevant to the issues addressed.

Added value for the CRISSUE-S activity consists of proposing and making available a list of transients to be analysed by coupled neutron kinetics/thermal-hydraulic techniques and of defining ”acceptability” (or required precision) thresholds for the results of the analyses. The list of transients is specific to the different NPP types such as PWR, BWR and VVER. The acceptability thresholds for calculation precision are general in nature and are applicable to all LWR. The creation of a database including main results from coupled 3-D neutron kinetics/thermal-hydraulic calculations and their analysis should also be noted.

The CRISSUE-S project is organized into three Work Packages (WP). The first WP includes activities related to obtaining and documenting relevant data. The second WP constitutes the State of the Art Report (SOAR) while the third WP concerns the evaluation of the findings from the SOAR and includes outcomes of the entire project formulated as recommendations, mainly to the nuclear power industry and to the regulator authorities. The present report is the result of the first WP and discusses the type of transients that are of interest in relation to reactivity initiated accidents in LWR NPPs and elaborates on the data needed for coupled 3-D neutron kinetics/thermal-hydraulic analysis and also on data needed to perform associated validations.

The report has been written to accomplish the objectives established in the contract between the EU and its partners. Expected beneficiaries include institutions and organizations involved with nuclear technology (e.g. utilities, regulators, research, fuel industry). In addition, specific expected beneficiaries are junior- or senior-level researchers and technologists working in the considered field of Research & Development and Application of coupled neutron kinetics/thermal-hydraulics.

This report is dedicated to the memory of Gianni Frescura, who as Head of the Nuclear Safety Division gave a strong support to this activity and arranged for the co-operation between OECD/NEA and this EC Project to be an effective one.

B.  
WORK PROGRAMME
B.1 
Neutron Kinetics / Thermal-Hydraulics Coupling in LWR Technology: Data Requirements and Databases Needed for Transient Simulations and Qualification
The main topic discussed in WP1, ref. [1], deals with the probabilistic safety assessment (PSA) and of associated outcome in relation to NPP transients revealing substantial core reactivity changes including Reactivity Initiated Accidents (RIA). Another topic concerns the modeling and related capabilities in the areas of thermal-hydraulics and 3-D neutron kinetics, with emphasis to needed ”input” and to specific modeling considerations. Some emphasis has also been given to transients measured in nuclear power plants, to complement the database of results that was created and described in the Annex I of the WP2 report. 

More specifically the WP1 report includes and discusses the following areas from the point of view of the data needed for performing the analysses and the necessary qualification:
· Probabilistic Safety Assessment
· Thermal-hydraulic System Simulation
· Three-Dimensional Neutronic and Fuel Simulation
· Coupling of Thermal-hydraulic System and 3-D Neutronic Codes
· NPP Modeling Data and Transient Data for Validation Purposes
· Data Added to the CRISSUE-S Database
B.2
Neutron Kinetics / Thermal-Hydraulics Coupling in LWR Technology: State-Of-The-Art Report

The description of the modelling and of the related capabilities in the areas of thermal-hydraulics, 3D neutron kinetics and nuclear fuel constituted the main topic for the WP2, together with the needed numerical techniques, ref. [2].  Emphasis has also been given to transient measured data in nuclear power plants, to ‘connected aspects’ in the technology (e.g. the simulator) and to the presentation of the licensing/regulatory point of view. Finally a database of results has been created.
The main subjects dealt with in the WP2 (these are analysed having in mind the objective of creating a state of the art on the subject) are:

· Thermal-Hydraulics 
· Neutron Kinetics
· Fuel
· Coupled Analyses
· Operator training
· Regulatory position  
· Database of results
B.3
Neutron Kinetics / Thermal-Hydraulics Coupling in LWR Technology: Achievements and Recommendations Report
The Work Package 3 of the CRISSUE-S project was designed having in mind the objective of summarizing the main finding of the activity and transferring g those to the expected beneficiary for the activity, ref. [3]. These include the main actors in nuclear technology that are the industry (both the vendor and the utility), the regulators and the research institutions (including universities). 

Therefore the main content of the WP3 report is reflected in the present report (section r C. hereafter). Even though the state of the art constitutes the main subject for the WP2, related conclusions and main findings are incorporated in each of the sections of WP3 report that are part of  the present report.

C.  
WORK PERFORMED AND RESULTS

C.1 
Introductory Remarks

The CRISSUE-S project started on January 1st 2002, with the aim of re-evaluating fundamental issues related to the safety technology of Light Water Reactors (LWR) involving interactions between Neutron-Kinetics (NK) and Thermal-hydraulics (TH).

Along with the needed emphasis on NK-TH analysis, the 12 CRISSUE-S partners organize their work in 3 work packages and in cooperation with VALCO project. The objectives of the project where established as it follows:

· Preparing the State-Of-Art

· Providing results of BE analysis in existing reactors

· Identifying areas of the NPP design where design/safety requirements can be relaxed

· Providing recommendations to target institutions

This report emphasizes the achievements of the project. It shows an important part of Work Package 2 conclusions and only some brief references to Work Package 1. It is structured as it follows.

As the importance of the fuel role is one of the findings of the project, a summary is included dealing with degradation of fuel during the transient or with other aspects like change of geometry, physic properties, cross-sections, etc. The whole summary is intended to show the existing connection between fuel engineering and neutron kinetics calculations. 

The Best Estimate approach along with the uncertainties analysis is also treated not only as methodology but also with some emphasis on uncertainty sources (sub-cooled heat transfer coefficient, pressure wave propagation, radiolysis, fuel safety margins…).

The specifications of the needed and the created data bases are relevant results of the project. They include not only the data base in general sense (code, NPP input, general report, initial conditions…) but also that of transients suitable for validation and results of its available analysis. Work Package 3 report focus on suitable codes as they become the guideline of the remaining items from the standpoint of utility decision makers. 

The requirements for analysis tools qualification will include the TH field (nodalisations and codes), the NK field (codes and cross-sections) and those related to coupling both kinds of codes.

The licensing status and the use of findings by industry allow the establishment of recommendations and final conclusions of the project.

C. 2  
Transients to be considered by Coupled Analyses
As a result of CRISSUE-S project a list of transients are recommended to be studied using a coupled analysis. Due to the existing plant configurations transient analysis become plant specific.

PWR transients

1) MSLB. Accident originated by the double ended guillotine break of one SL. Positive reactivity is caused by the cooling of the primary water following depressurisation of the SG. The ‘plug’ of cold water typically reaches the core a few seconds after the break occurrence in the steam line. Regional core power increase may occur owing to partial mixing in the RPV down-comer of cold water from affected SG with ‘hot’ water from intact SG. Potential ‘regional’ nature of the transient and ‘amount’ of introduced positive reactivity justify the coupled analysis. HZP and FP initial conditions can be investigated at BOC and EOC conditions.

2) LOFW-ATWS. Blockage of FW pumps also originated by ‘partial station blackout’ causes LOFW. Primary loop temperature increase and moderator and Doppler neutron feed-backs contribute to power decrease. The ATWS analysis is deemed necessary considering the (relatively high) accident frequency.  The accident scenario originated by the MSIV closure, again with the ATWS condition (i.e. MSIV closure-ATWS) could be studied with similar assumptions (apart from the initiating event) as the LOFW-ATWS. 

3) CR-expulsion. ‘Regional’ reactivity increase is expected following CR-expulsion. This justifies the application of the 3-D coupled techniques. The highest worth CR should be considered. HZP and FP initial conditions can be investigated at BOC and EOC conditions.  Expulsion of CR banks or of group of CR can be of interest. The CR expulsion is connected with an SBLOCA due to the damage of the holding mechanism for the expulsed rod (this is mostly not considered in the current analyses). 

4) LBLOCA-DBA. The accident is originated by the double ended guillotine break of one CL at a location between the RPV and the MCP. The accident constitutes a pillar in the safety demonstration and in the licensing of any LWR, with main reference to the evaluation of the ECCS design and, for this reason, is part of the ‘official’ NPP FSAR. The proposal for 3-D neutron kinetics – thermal-hydraulic analysis is mostly connected with the need to quantify the conservatism introduced by the ‘highly conservative’ Peak Factors (PF) for linear power that cause high values for PCT. The use of the advanced coupled neutron kinetics – thermal-hydraulic techniques brings to the removal of that conservatism and emphasizes the industrial relevance of the same techniques. A specific LBLOCA-RIA occurs in the case of positive moderator temperature coefficient, what is possible in principle at BOC with high boron concentration. 

5) Incorrect Connection (start-up) of an Inactive (idle) Loop. The inactive loop is assumed to have de-borated water in the loop seal having a volume consistent with the system geometry. This transient is representative of transients originated by the presence of boron in the primary loop (see also the SBLOCA-ATWS, below).

6) MSLB-ATWS. The MSLB constitutes a DBA transient (see description above). The ATWS feature is not justified by any PSA study. Rather, the recommendation for the 3-D coupled analysis derives from the bounding nature that this transient might have (i.e. in terms of ‘input reactivity’ for the core) and from the consideration that core integrity can be predicted for such extreme situation.

7) SBLOCA-ATWS. This is a TMI-type accident originated by ‘small’ loss of integrity of the primary loop. The relatively high frequency of occurrence justifies the ATWS condition. Positive reactivity insertion can be assumed to come from de-borated water coming from any ECCS, i.e. HPIS and ACC (or SIT) and LPIS. The amount of ‘fresh’ (un-borated) water injection should be according to the individual plant features and maintenance programs.      

BWR transients

1) TT without condenser bypass available. TT constitutes a (relatively) frequent event for BWR operation. Positive pressure wave propagates from the turbine isolation valve to the RPV and reaches the core from the top (e.g. across the steam separator and dryer) and from the bottom (e.g. across the down-comer and the lower plenum). Void collapse causes positive reactivity insertion and power excursion typically stopped by scram occurrence. Opening of condenser bypass valves makes milder the effect of the pressure wave propagation, but this effect is neglected in the proposed scenario. 

2) LBLOCA-DBA. The rupture of one recirculation line (if present) originates the accident. The regulatory framework and the reasons for the analysis are the same as discussed in relation to PWR (see above).

3) CR-expulsion. The same considerations made for PWR apply here.

4) FW temperature decrease – ATWS. Malfunction of FW pre-heaters (e.g. sudden depressurisation in one pre-heater on the heating side) and of FW pumps (e.g. DC level control system) may cause FW temperature decrease that reflects in colder water at core inlet. This creates the potential for reduction of the steam occupied volume into the core and consequent increase in moderation and in fission power. This partly covers the event FW flow-rate increase (see also below).   

5) MCP flow-rate increase. The flow-rate increase may be caused by malfunction of valves installed in the MCP lines or by spurious signal controlling the pump speed (whatever realistic for the concerned NPP). This partly covers the event FW flow-rate increase.

6) MSIV closure – ATWS. The closure of the main isolation valves creates a pressure pulse (same situation as TT) that causes void collapse into the core and reactivity excursion. The ATWS condition must be considered as a ‘bounding condition’ in safety analysis. The application of the 3-D neutron kinetics – thermal-hydraulic technique has the potential to show that even in such extreme and unrealistic (low probability) conditions the safety margins embedded into the system design allow recovery of the core.

7) Stability analysis.  Stability performance of BWR has been deeply investigated during the entire nuclear era. Synthesis reports have been issued, and recent published analyses show the applicability of the 3-D coupled techniques. Use of different fuel types in the same core makes more valuable and necessary the proposed investigation. Recommended transient can be originated at nominal power and include MCP trip that brings the plant into the ‘exclusion region’ of the BWR flow map. Transient analysis should go on till the establishment of NC steady state roughly at 50% nominal core power and 30% nominal core flow. The FW and the SL flow-rates should be varied according to the core power and the RPV pressure should be kept (nearly) constant during the simulation. Control systems for RPV pressure and DC level (and various BOP components) can be simulated or less: their role in determining the stability performance of the system should be evaluated. 

8) Stability analysis – ATWS. The same analysis as before shall be performed assuming failure of the scram system. Though this condition is beyond the DBA boundaries owing to the low probability of occurrence, results can be useful to designers and to safety analysts to optimise EOP and to better understand safety margins of the NPP.     

A similar list has been established for VVER plant and can be found in section 1.4 of the Work Package 2 report.

Despite of what has been said in the paragraphs above, each licensing process of a specific plant, has specific transients that become crucial depending on the reactor history and cycle design. Knowing the list of them in each case is a valuable information to focus on transients really suitable to be analysed. 
Additional information in relation to the transients to be studied for coupled analysis can be found on sections 1.2, 1.3 and 1.5 of Work Package 2 report as well as in sections 2.2, 2.3 and 2.4 of Work Package 1.

C. 3 
Thresholds of Acceptability for Coupled Codes Results
The precision that is needed for any code-calculation must derive from the specific application. However, the capabilities of computational tools including the computer power may have a strong role in assigning a target precision. Owing to this reason and to the continuous (in the last 30-50 years) fast growth of both computer power and of capabilities of numerical techniques, ‘target precision’ is seldom requested in complex code applications to the nuclear technology. 

Notwithstanding the above an attempt is made hereafter to formulate criteria and to define thresholds of acceptability for the results of coupled 3-D neutron kinetics thermal-hydraulics calculation. A straightforward process is pursued: a minimum reasonable number of ‘quantities of interest’ is identified at first, requested error is assigned based on engineering judgment that takes into account of the current state of the art. A short description of the suitable level of detail requested for coupled calculation is given before the selection of quantities of interest and the related acceptability thresholds.

Quantities of interest

A variety of quantities of interest for the design and the safety evaluation of LWR are the output of coupled 3-D neutron kinetics thermal-hydraulicss calculation. These range from the Keff, to the boron concentration to reach criticality, to the worth of CR, to the transient pressure, the fuel temperature, the flow-rate, the level (e.g. into the PRZ), the amount of radioactive liquid discharged from a relief valve (SRV or PORV). The identification of these quantities is connected with the transient type (e.g. ATWS or LBLOCA), with the application type, notably licensing or design analysis and is related to the duration of the transient. Definitely, each application  is associated with a set of ‘quantities of interest’.  A minimum-reasonable set of ‘quantities of interest’ is defined below making reference to a transient duration of the order of 100 s. The following quantities are selected and related ‘point-values’ are considered:

· [Quantity 1 and 2] Peak pressure in RPV (UP location) and in PRZ (if applicable), related FWHM (if applicable) and time of occurrence,

· [Quantity 3] Peak total core power, related FWHM (if applicable) and time of occurrence,

· [Quantity 4] CHF (or DNB) occurrence time,

· [Quantity 5] PCT and time of occurrence, 

· [Quantity 6] Maximum Fuel Temperature (MFT) and time of occurrence,

· [Quantity 7] Total thermal energy released to the fluid during the transient (TTEF = Total Thermal Energy released to the Fluid),

· [Quantity 8] Maximum % of core, in terms of heat transfer area (HTA) of the active region where, at any time, rod surface  temperature > 1000 K occurs (CRHST = Core Region at High Surface Temperature),    

· [Quantity 9] Maximum % of core in terms of volume occupied by fuel pins in the active region where, at any time, fuel  temperature > 3000 K occurs (CRHFT = Core Region at High Fuel Temperature).    

Acceptability thresholds for the quantities of interest

The definition of acceptability thresholds encounters the same difficulties mentioned in the previous paragraph for the quantities of interest. The dimension of the core, therefore including the nominal power and the power generated per unit volume, and various other nominal operating conditions (e.g. nominal pressure, set-point for valves opening) may also affect the identification of thresholds of acceptance.

However, the errors that are acceptable (acceptability thresholds) for the identified quantities are defined hereafter. In the present approach it is assumed that the overall error for a ‘point-value’ quantity  is the combination of two independent contributions: the “quantity” errors and the “time” error. Therefore, the predicted point-value quantity stays in a rectangle whose geometric center is the BE prediction and whose edges are given by the “quantity” and the “time” error  values.

· [Quantity error, situation ‘a’] For pressure pulses characterized by FWHM < 0.1 s in reference-BE evaluation, acceptable threshold error is 10 % nominal pressure of the considered system,

· [Quantity error, situation ‘b’] For pressure pulses characterized by FWHM ( 0.1 s in reference-BE evaluation, acceptable threshold error is 2% nominal pressure of the considered system,

· [Quantity error, situation ‘a’] For core power pulses characterized by FWHM < 0.1 s in reference-BE evaluation, acceptable threshold error is 100% nominal power or 300% initial power of the considered system, whatever is smaller,

· [Quantity error, situation ‘b’] For core power pulses characterized by FWHM ( 0.1 s in reference-BE evaluation, acceptable threshold error is 20% nominal power or 100% initial power of the considered system, whatever is smaller,

· [Quantity error, situation ‘b’] For PCT, acceptable threshold error is 150 K (larger errors can be tolerated for BE-prediction of PCT below 1000 K),

· [Quantity error, situation ‘b’] For  MFT, acceptable threshold error is 200 K,

· [Quantity error] For TTEF acceptable threshold error is 10% of energy released to the fluid in nominal conditions or the 100% of energy released to the fluid at the actual initial power, during the considered transient duration, whatever is smaller,

· [Quantity error] For CRHST acceptable threshold error is 10% of core HTA,

· [Quantity error] For CRHFT acceptable threshold error is 10% of core pin volume,

· [Time error, situation ‘a’] The acceptable time error that can be associated to the prediction of time of occurrence of Quantities 1 to 3 is 100% of the BE value,

· [Time error, situation ‘b’] The acceptable time error that can be associated to the prediction of time of occurrence of Quantities 1 to 6 is 20% of the BE value,

· [Time error, situations ‘a’ and ‘b’] The acceptable time error that can be associated to the prediction of FWHM for Quantities 1 to 3 is 20% of the BE value.

The proposed “acceptable threshold error” are consistent with the expected capabilities of current computational tools assuming the best practice in their application.

C.4 
The Role of Fuel

An significant part of CRISSUE-S project findings are related with the role that fuel plays in the context of safety critical issues. For this reason a special chapter of Work Package 2 report and also a complete section of Work Package 3 are devoted to explain the relevance of fuel properties and fuel failure in coupled analysis. 
Reactor engineers within nuclear power plants responsible organization are today devoted to determine and ensure the correct behaviour of fuel in operation conditions that could become more sever than the current ones.

Different issues are considered. Among them: increasing discharge burn-up of used fuel elements, high power peaks, high evaporation rates, high crud deposition products or chemistry programs with high pH and lithium. All these issues are safety related and could become critical. That is why safety research has to focus on avoiding clad corrosion in order to maintain the integrity of fuel rods and ensuring dimensional stability and absence of failures.

The use of new clad materials, such as Zirlo, or the implementation of intermediate flow-mixing grids (IFM) and other factors have allowed a relevant discharge burn-up increase.

It seems clear that fuel will work in a near future under operating conditions more sever than today. Because of this last statement, it will also be necessary to check the behaviour of the plant in safety scenarios taking into account today trends.

The change of properties and the degradation of fuel, mainly during its life but also during the transient itself, produces variations of fuel geometry as well as the corresponding cross-sections. These changes obviously have an impact on NK calculations and on the subsequent safety analysis.

Thermo-physical properties of materials for LWR

Recommended data for the thermo-physical properties of nuclear materials have been published in the MATPRO-publications. The last issue of MATPRO-data, in the SCDAP/RELAPS/MOD2 Code Manual from 1990, contains descriptions of material properties subroutines available in that data base. The adequacy of the available data on the appropriate physical and chemical properties of some nuclear materials has been reviewed in the report EUR-12404 (1989) published by the Commission of European Communities. Furthermore, a variety of other recommendations have been made for the thermal conductivity and specific heat capacity of fuels. 

Fuel failure mechanisms

Water reactor fuel continues to perform reliably in power reactors around the world. However, fuel failures from knows mechanisms still occur, occasionally with a significant impact on plant operation, and the current average fuel rod failure rates of around 10-5 are still high compared to the "zero failure" goal, which in today's understanding should correspond to a failure rate near 10-6. Improving fuel reliability beyond current levels will be even more challenging for countries involved with programs to further increase fuel discharge burnup. A good understanding of fuel performance is essential for identifying  the root causes of failures, and for defining remedies at the design, manufacturing and operational levels.

The IAEA review has two major aims. The first addresses the above technical back-ground with the aim of updating and supplementing the earlier IAEA publication of 1979. The second aim for this study is to provide a combined presentation of the worldwide experience in this field in order to promote an exchange of information and future co-operation.  The reactors covered by this study are "western" type boiling and pressurized light water reactors (BWR and PWR), and Soviet type pressurized light water reactors (WWER). The acronym LWR will refer hereafter to the three types, BWR, PWR and WWER.

Recent surveys on fuel failures in general or related to regional experience have been given in several papers. In a comparison of the situations in 1979 and today, two factors are noteworthy. Firstly, the fuel rod failure rates in LWR have been significantly reduced, on average by approximately one order of magnitude from the range above 10-4 to levels near 10-5, i.e. a few rods per 100.000 rods in operation. Secondly, it is interesting to see that a majority of the mechanisms of earlier fuel failures are till active, mostly in combination with new root causes and contributing factors.

Sections 3.3 and 3.4 of Work Package 2 report provide an explanation on the mechanisms and root causes of fuel failure along with different detail on its relation with coupled analysis. A list of the identified mechanisms follows:

Manufacturing defects, Primary hydriding, Pellet-clad interaction, Corrosion, Dry-out, Cladding collapse, Grid-rod fretting, Debris fretting, Baffle jetting, and Assembly damage.

Final remarks on fuel role

Important operating initiatives are taken to prevent fuel failure in plant operation. Some of them are related to operating procedures like: the surveillance of coolant activity, the guidelines for power changes and load following operation, the strategies for prevention of severe degradation or water chemistry controls. Some others belong to the field of fuel handling like: fuel loading/unloading practices and storage/disposal of failed fuel.

All these initiatives are having positive results and producing a better fuel performance. Besides this main outcome, the improved knowledge on fuel behavior has to be utilized as a necessary feed-back leading to a more accurate treatment of the key parameters of safety analysis. CRISSUE-S project identifies the need of coordination between the knowledge reached through operating practices concerning fuel and the future techniques of coupled NK-TH safety analysis.  

C.5 
The Best-Estimate Approach

C.5.1 
Methodology 
The word ‘uncertainty’ and the need for uncertainty evaluation are connected with the use of BE codes instead of ‘conservative’ codes or assumptions in the code application. The application of coupled 3-D neutron kinetics thermal-hydraulics codes implies the choice of the BE approach. Nevertheless, hereafter a short discussion is provided in relation to the need for BE, the difference between BE and conservative, the origin of uncertainties and the current status for uncertainty evaluation. Additional details can be  found in section 2.6 of Work Package 2 report and corresponding references.

The selection of a best estimate analysis in place of a conservative one depends upon a number of conditions that are away from the analysis itself.  These include the available computational tools, the expertise inside the organization, the availability of suitable NPP data (e.g. the amount of data and the related details can be much different in the cases of best estimate or conservative analyses), or the requests from the national regulatory body. In addition, conservative analyses are still widely used to avoid the need of developing realistic models based on experimental data, task that may reveal ‘un-realistic’ in the case of BDBA, or simply to avoid the burden to change approved code and/or the approaches or procedures to get the licensing.

The conservative approach does not give any indication of the actual margins between the actual plant response and the conservatively estimated response. By contrast, the uncertainty estimate provided in the best estimate approach is a direct measure of such margins. As a result the best estimate approach may allow for the elimination of unnecessary conservatism in the analysis and may allow the regulatory body and plant operating organization to establish a more consistent balance for a wide range of acceptance criteria. A conservative approach does not give any indication about actual plant behaviour including time-scale for preparation of emergency operating procedures, or for use in accident management and preparation of operation manuals for abnormal operating conditions.

Although the acceptability of the approach to be used for an accident analysis needs to be defined by the regulatory body, the use of totally conservative approaches (conservative models, input data and plant conditions) results unwarranted nowadays, given the broad acceptance of best estimate methods (e.g. mature best estimate codes are widely available around the world, an extensive database exists for nearly all power reactor designs and best estimate plant calculations are well documented). The use of totally best estimate approach implies “the difficulty” of quantifying code uncertainties for every phenomenon and for every accident sequence. 

C.5.2
 Uncertainties 
Uncertainty analyses include the estimation of uncertainties in individual modeling or of the overall code, uncertainties in representation and uncertainties in plant data for the analysis of an individual event. Scaling studies to quantify the influence of scaling variations between experiments and the actual plant environment are included in this definition. In some references, code scaling and uncertainty analysis are identified separately. These concepts are applicable to any of the CSC, NKC and THSC. 
A number of uncertainty evaluation methods proposed by different institutions are mentioned in ref. [2]. 
CIAU method and its extension

All of the uncertainty methodologies suffer of two main limitations:

· The resources needed for their application may prove to be prohibitive, ranging to up to several man-years;

· The achieved results may be strongly methodology user dependent.

The idea at the basis of the CIAU can be summarized by three items:

· Build-up of NPP status: each status is characterized by the value of six relevant quantities (or phases) and by the value of the time since the transient start. Each of the relevant quantities is subdivided into a suitable number of intervals that may be seen as the edges of hypercubes in the phase-space. The transient time or duration of the transient scenario is also sub-divided into intervals.

· Association of uncertainty with NPP status: accuracy values derived from the analysis of experimental data are associated to each NPP status.

· Use of the method: at each time, the CIAU code-calculation result is associated to a time interval and to a hypercube, i.e. a NPP status, from which the uncertainty values are taken and associated with the current value of the prediction.

The CIAU idea can be applied with any uncertainty method. In other words, any existing uncertainty method (e.g. CSAU, GRS method, etc.) can be used to generate uncertainty values thus ‘filling’ the hypercubes and the time intervals. The idea at the basis of the current CIAU is connected with the status approach.


First, quantities have been selected to characterize in a multidimensional space the thermal-hydraulic status of a LWR during any transient. Then, accuracy has been calculated from the analysis of experimental data. The combination of accuracy values and time intervals allows the derivation of continuous uncertainty or error bands enveloping any time dependent variables that are the output of a system code calculation. 

Relap5/mod3.2 system code and UMAE uncertainty methodology have been coupled to constitute the CIAU. Therefore, the uncertainty has been obtained from the extrapolation of the accuracy resulting from the comparison between code results and relevant experimental data: these may be obtained from integral test facilities as well as from separate effects test facilities. 

Within the CRISSUE-S framework, the methodology has been extended to 3D neutron kinetics thermal-hydraulics calculations.

A number of input parameters connected with neutron kinetics calculations are uncertain:

· rod worth ± 10 %  or ± 15 %  (depending on reference)

· fraction of delayed neutrons (β) ± 5 % 

· Doppler coefficient  ± 20 % 

· moderator coefficient  ± 30 %  

· fuel heat capacity  ± 10 %  (actually this is also a relevant thermal parameter)

· boron reactivity coefficient ± 15 % 

· change in the reactivity per unit change in the fuel and moderator temperature when fuel and moderator are at the same temperature ± 0.36 10-4 /°C 

· critical boron concentration at 100% core power ± 50 ppm 

· power distribution (at intermediate level and at 100 % power) ± 0.1 * relative power density for each measured assembly power 

In a static calculation, the main output parameter is constituted by the k(. More detail on the subject can be found in section 2.12 of Work Package 2 report and the related references. The reported values can be interpreted as ‘minimum’ acceptable values for the error in calculating k(. 

Basically, the demonstration of the feasibility of the approach has been achieved and sample results related to the BWRtt transient in the Peach Bottom NPP, are shown in Annex 1 of Work Package 2 and related references. 

C. 5.3 
Sources of Uncertainty

C. 5.3.1
Fuel related
As it has been said in the introduction of this document, fuel is playing a very relevant role in the subject of critical safety issues related to the analysis of nuclear power plant behaviour using coupled NK-TH codes. That is why a special (section 3) has been devoted to clarify such significance.

Although the purpose of the contents of section 3 is clearly related to fuel management, an implicit message is derived from it: fuel is probably the main source of uncertainty in the context of coupled predictions.

Traditionally, in conservative calculations, assumptions are made to take into account the uncertainties related to fuel properties, and the final analysis becomes penalized and allows less flexibility for operation.

Each and every subject listed or summarized in section 3 results in an uncertainty that is added to the key parameter involved. Among fuel uncertain parameters, some are clearly NK related and some others TH related. The variation of the most of them have an impact on both NK and TH analysis due to feed-back.

Some other NK-TH parameters and phenomena characterized as source of uncertainty and not addressed in section 3, are listed below:   

Radiolysis in fast reactivity transients, Dynamic sub-cooled boiling, Dynamic CHF, Volume void weighting on HT-surface for two-fluid models, and  Spacers with mixing vanes,

C.5.3.2   Related to Other Phenomena or Components
Valve characteristics

Valve characteristics, i.e. valve area changes as for instance function of time with associated pressure losses, have to be provided as part of the valve component input. The exact characteristics of real valves are difficult to attain and thus the effects often have to be evaluated from sensitivity analyses. In relation to reactivity changes important influences from the valve operations can be the BWR core pressure variations at closure of the turbine stop valve and especially the associated pressure wave propagation through the steam line and into the RPV. The pressure wave will become more pronounced if the valve area change is incorporating a high valve area time derivative, i.e. from a pressure wave influence point of view the often used linear area change will provide non-conservative results.

Frictional and discrete pressure losses

Accurate pressure loss distribution in the T/H system is one essential prerequisite in order to be able to calculate an accurate flow distribution which in turn is necessary for having an adequate reactivity response. The frictional pressure losses are usually included by assigning appropriate roughness to various surfaces in contact with the fluid. It is envisioned when it comes to the core that the roughness is influenced by the time period during which the fuel assembly has been loaded into the core, i.e. by the burn-up, with an increased roughness with time due to the growth of the oxide layer. It is also realized that the detachment of possible rod surface vapour layer, as caused by spacers with mixing vanes as indicated above, can influence the resulting downstream frictional pressure loss. This type of phenomenon is rarely simulated by the T/H system codes.

Usually the discrete loss coefficients are assigned a constant value, but for the fuel assembly spacers there are indications that a weak Reynolds number dependence is more adequate with the loss coefficients decreasing with increasing Reynolds number.

Phase separation at tees

The phase separation phenomena at tee components can have a dominant influence on the course of the system depressurisation rate. So will for a BWR steam line break a perfect separation result in maximum depressurisation while minimizing the loss of inventory. Reaching low pressure while maintaining a high liquid inventory may be non-conservative (for instance by retaining the fuel temperature well below any critical levels). Activities are underway by USNRC to review existing models and to evaluate and possibly improve their capabilities under extended ranges of conditions.

High transient thermal flux

As consequence of CR expulsion, high local thermal flux occur. Sub-cooled voids can be formed in a bulk of ‘high speed’ liquid. Void formation create volume increase in initially nearly incompressible fluid environment like the RPV of a PWR. Local thermal power exchange may reach values one order of magnitude larger than  in nominal conditions and pressure may locally increase up to several MPa. DNB is expected. Validation of convection heat transfer correlations is questionable under these conditions.

Positive pressure pulse propagation

In a BWR core it causes void collapse and consequent positive reactivity excursion. This creates the condition for sudden re-evaporation of the condensed liquid. Range of validity of convection heat transfer correlations is again questionable under these conditions. Thus a careful consideration of the Courant limit, in these cases based on acoustic wave propagation, and of the calculation node length has to be adopted. The donor-cell differential scheme has a strong tendency to attenuate pressure waves when using node lengths as usually applied in ”bulk” flow transient scenarios and a careful evaluation of nodalisation and usage of time step sizes can possibly ameliorate the situation. The pressure wave propagation into the steam dome of the BWR through the dome outlet nozzle has to be mentioned. This transmission, which is also accompanied by a reflection wave back into the steam line, is rarely simulated, and the resulting dome pressure response must be regarded as very uncertain.
The CR movement creates local fluid displacements that locally may be significant.

C.5.3.3   Related to Models and Codes

Heat transfer modelling inside pin and fuel modelling

The heat transfer phenomena inside the fuel pins comprise heat conduction in the fuel pellets, heat transfer across the gap between fuel pellets and cladding inside surface, and heat conduction across the cladding thickness. The combination of these effects along with the geometrical fuel pin design will influence the fuel pin overall time constant at power variations, however the heat transfer across the gap (”gap conductance”) will have the greatest influence. All the effects are much dependent on the fuel pin burnup and will consequently also have a variation in the axial direction. It is noted that with normal ”heat structure” modelling practice these axial variations can not be taken into account. A possibility could be to axially use a stack of different ”heat structure geometry” combinations, however this would impair the usage of the ”moving mesh” capability in cases the reflood simulations are needed.

The list of pin heat-conduction and fuel-related phenomena or related computational aspects that may require further investigation to validate the results of coupled neutron kinetics thermal-hydraulic calculations includes the following:

1) Minimum number of concentric rings for the fuel rod that bring to the convergence of results for CSC, NKC and THSC (this number must be consistent in the three steps of the analysis). The suitable number of rings for the gap should be identified, too.

2) Pellet gap performance during the transient with main reference to variations in physical properties and geometry. The evaluation of such aspects is not within the typical current NKC and THSC capabilities.

3) Fuel deformation and change in physical properties during the transient (namely ‘steep’ power rise). Coupling between THSC and ‘fuel’ codes might be needed.

Neutron transport and diffusion

The state of the art of currently used multi-dimensional neutron kinetics models for LWR calculations of core time dependent spatial neutron flux distribution includes the utilization of 3D neutron diffusion equation based on two neutron energy groups and with six groups of delayed neutron precursors. This has found to be adequate for steady-state applications and for those transient applications where direct validation has been possible. The use of ADF has been proven to be sufficient for several applications. It is also realized that the utilization of MOX-fuels with its higher contents of Pu requires additional neutron energy groups to be included for accurate simulations. The Pu isotopes have high absorption and fission resonance at around 1 eV (Pu-240 absorption) and from 100 eV up to keV (Pu-239, Pu-241 absorption and fission).

The major calculation features of the neutron diffusion models, include the ability to perform eigenvalue calculations (keff), transient flux calculations, Xenon transient calculations, decay heat calculations, depleting (burn-up) calculations, and adjoint calculations. Also pin power reconstruction capabilities are available to obtain pin power and associated intranodal neutron flux distributions from the calculated nodal fluxes. The 3D capability provides the basis for realistic representation of the complete reactor core although provisions are included to use appropriate symmetry sections, like half and quarter core parts for computational efficiency. Carefully selected boundary conditions for the symmetry planes are paramount for adequate calculation results in those cases. Also 1D capabilities are usually available for simulation of transients with predominant axial neutron flux variations.

Important data for the neutron diffusion calculations apart from pure geometrical descriptions of various core parts include tabulated macroscopic cross-sections as function of T/H and fuel parameters, boron concentration, and of control rod positions (worth, used banks, etc) and microscopic cross-sections for Xe and Sm including corresponding dependencies. Other data are decay constants and the ADF for the fuel assemblies’ four sides.

The list of neutron kinetics phenomena or related computational aspects that may require further investigation to validate the results of coupled neutron kinetics thermal-hydraulic calculations includes the following:

1) Identification of suitable number of neutron energy groups.

2) Influence of resonance absorption cross section in ‘individual’ layers of pellets (partly connected with the previous item).

3) Systematic identification of influence of material discontinuities (e.g. due to the presence of fuel box, CR, at the border between reflector and core active region, etc.).

C.6 
Needed Data Base and Suitable Codes

Although the needed database for NK-TH calculations has to include also some other items besides the code itself, it seems interesting to focus on codes in this summary. Details on NPP input, initial conditions or general plant description can be found in Work Packages 1. The interest of having focused on codes has to do with utilities decision makers. Once the decision of using a code is made, the NPP input is created thinking of the chosen code, and even plant details and initial conditions are explicitly recorded following the interaction with the code user. 

Although the responsible for plant operation wants to have results from more than one (normally two) calculation options, this section is not the right place to discuss the issue. It is really important to have a common plant description as a base to build input decks for different codes, but the point can be treated in another context. Section 9 of this report (use of industry) explains the most relevant part of the issue. 

Complex codes are needed for three steps of the application of the 3-D coupled techniques:

· Codes for deriving suitable neutron kinetics cross sections (CSC = Cross Section Code).

· Thermal-hydraulic system codes (THSC = Thermal-Hydraulic System Code).

· Neutron kinetics codes (NKC = Neutron Kinetics Code).

Codes described here are internationally known and suitably qualified. The list of codes is by no mean exhaustive but serves as an indication of the type of codes available today within the area of coupled THSC - NKC. Features and capabilities of those codes are mentioned in the following sections. Details can be found in the reported references

The consistent application of CSC, THSC and NKC is required to perform a full 3-D coupled neutron kinetics thermal-hydraulic calculation. However, the CSC can be used ‘out of the line’ and THSC and NKC must be coupled and interact ‘at each’ time step.  

‘Cross-section’ codes

Casmo

The widely used CASMO cross-section parameterisation model attempts to model the cross-section cross term dependence involving an approximate type of cross-section representation. Each cross-section can be evaluated as a summation of base and partial values. The base cross-sections represent the burn-up dependence (exposure, spectral history and control history) while the partial cross-section represent the instantaneous dependence on local feedback parameters. 

Thermal-hydraulics system codes

Athlet

The thermal-hydraulic computer code Athlet (Analysis of THermal-hydraulics of LEaks and Transients) is being developed by the Gesellschaft fuer Anlagen- und Reaktorsicherheit (GRS) for the analysis of anticipated and abnormal plant transients, small and intermediate leaks as well as large breaks in light water reactors.

It has a highly modular structure, and allows an easy implementation of different physical models. Athlet is composed of several basic modules for the calculation of the different phenomena involved in the operation of a light water reactor: 

Relap5 USNRC version
This is a thermal-hydraulic system code extensively used for the analysis of any kind of transient in LWR. The code is based upon the solution of six partial differential equations that are coupled with (or that need for their solution):

· a wide range ‘Heat Transfer Surface’ for the determination of the HTC,

· the equations for the conduction heat transfer into the solid,

· a variety of constitutive equations (e.g. interfacial drag),

· a variety of ‘external models’ (e.g. two phase critical flow, pump, separator),

· the equations for ‘tracking’ various non condensable gases,

· the equation for ‘tracking’ boron into the system, 

· 0-D neutron kinetics equations.

Material properties are embedded into the code, but can also be supplied by the user. The numerical solution method has been specifically adapted for the code and is based upon the use of semi-implicit finite-difference technique. The code is capable to model the primary and secondary circuits (where applicable) of NPP as well as all the components belonging to the BOP including the related actuation logic. 

The code is classified as a 1-D code, though ‘fictitious’ 3-D nodalisations (input decks) can be set-up to simulate three-dimensional flow configurations in open zones.

Relap5-3D © DOE version
All the discussion in the previous paragraph related to Relap5 NRC, applies here. It can be added that Relap5-3D © has the capability to apply in selected zones of the NPP the 3-D thermal-hydraulic general model. The NESTLE 3D neutron kinetics is embedded in this RELAP computer code version.   

Cathare-2 CEA code
All the discussion in the previous paragraph related to Relap5 NRC, applies here. It can be added that Cathare code was directly developed for PWR plant though it has been recently applied to the analysis of transients in WWER and BWR NPP. Related to Relap5, a different numerical solution method is adopted and a different structure of the input deck must be set-up by the user. The code has the ‘design’ capability to simulate the containment. 

The code Cathare is modular, several basic modules may be assembled to model the primary and the secondary circuits of any Pressurized Water Reactor or of any analytical test rig – separated effects – or integral test rig – system effects -. 0D, 1D and 3D modules are available. All of those modules can be connected to walls, exchangers and fuel rods – radial conduction, thermo mechanics -. A 2D conduction calculation is generally done to cope with the quenching of a hot reactor core during a reflooding process. Other sub-modules are used to compute point kinetic neutronics, pumps speeds, accumulators, sources and sinks. All the modules above use the 2-Fluid Model to transport steam-water flows mixed to four non-condensable gases. Thermal and mechanical non-equilibrium are described through mass, energy and momentum balance equations written for each phase. 

TRAC-PF1

Los Alamos National Laboratory (LANL) developed the original TRAC thermal-hydraulic code in the mid 70s for PWR analysis. TRAC-PF1 is considered as probably the one of the most advanced thermal-hydraulic code because of its full six equation, two fluid model of the vessel component, so that accurate modeling of the transient can be accomplished. The code can treat a non-condensable gas in a vapor field as well as dissolved solute in the liquid field. TRAC-PF1 code is a best-estimate system transient analysis code, which has a 3D thermal-hydraulic analysis capability. A modified version of TRAC-PF1/MOD2 version 5.4 is currently being used at the Pennsylvania State University (PSU). The Version 5.4 incorporates a one-dimensional decay heat model that dynamically computes the decay heat axial shape during the transient. The code solves the general transient two-phase coolant conditions in one, two, or three dimensions using a realistic six-equation, two-fluid, finite-difference model combining three-dimensional vessel hydrodynamics and 1D balance-of-plant modeling. Two-dimensional treatment of fluid-wall heat transfer is incorporated through ROD and SLAB components. ROD component provides the treatment of power generation and its transfer to the coolant. The six-equation representation of the two-phase flow conditions, in conjunction with specialized empirical modes for a variety of PWR primary and secondary-loop components and control systems, allows TRAC-PF1/MOD2 version 5.4 to accurately model both mild and severe T-H transients. 
TRAC-M  
The United States Nuclear Regulatory Commission (US NRC) is currently consolidating the capabilities of its four T-H codes (TRAC-P, TRAC-B, RELAP, and RAMONA) into a single code. The goal of the efforts is to combine the capabilities of the current suite of codes while reducing the maintenance and development burden. The user community will then be able to focus on one code instead of four, thereby enhancing the knowledge base. A modernized and modularized TRAC-P code, now called TRAC-M, serves as a basis for the consolidation. The architecture has been revamped and the language migrated to FORTRAN90 to produce a more modular, readable, extendable and developer-friendly code. A neutronics package has been coupled to TRAC-M using parallel virtual machine (PVM) to provide a 1D and 3D kinetics models without having to add this functionality to the TRAC-M code itself. This allows the ability to improve the neutron kinetics or T-H models in TRAC-M independently.  

TRAC-BF1
TRAC-BF1 is a best estimate full system thermal hydraulics code system for a boiling water reactor. The two-fluid flow models are solved in one- and three-dimensions. The code is modular in nature and based on component models.
POLCA-T

POLCA-T is a coupled 3D core neutron-kinetics and system thermal-hydraulics computer code. The code is able to perform steady state and transient analysis of BWR. The code is based in different extend on models and tools for BWR and PWR analysis used in POLCA7, BISON and RIGEL codes. The code utilises new advanced methods and models in neutron kinetics, thermal-hydraulics and numerics. 

Neutron kinetics codes 

Dyn3d
The code Dyn3d was developed at FZ Rossendorf and is used for investigations of steady state and reactivity transients in cores of thermal power reactors with hexagonal or quadratic fuel assemblies. The 3-dimensional neutron kinetics model HEXDyn3d of the code is based on nodal expansion method for solving the two-group neutron diffusion equation. The thermo-hydraulic part FLOCAL consists of a fuel rod model and a two-phase flow model describing coolant behaviour and based on four differential  balance equations for mass, energy and momentum of the mixture and mass balance of the vapor phase. Several safety parameters as temperatures, DNBR and fuel enthalpy are evaluated. Macroscopic cross sections depending on thermo-hydraulic parameters and boron concentration are input data of the code.

NEM 

NEM is a 3-D multi-group nodal code developed and used at The Pennsylvania State University (PSU) for modelling both steady state and transient core conditions. The code has options for modelling of 3-D Cartesian, cylindrical and hexagonal geometry. This code is based on the nodal expansion method for solving the nodal equations in three dimensions. It utilizes a transverse integration procedure and is based on the partial current formulation of the nodal balance equations. The leakage term in the one-dimensional transverse integrated equations is approximated using a standard parabolic expansion using the transverse leakages in three neighbour nodes. The nodal coupling relationships are expressed in partial current formulation and the time dependence of the neutron flux is approximated by a first order, fully explicit, finite difference scheme. This method has been shown to very efficient although it lacked the precision of the advanced nodal codes. Recently an upgrade of the method has been completed, replacing the fourth order polynomial expansion with a semi-analytical expression utilizing a more accurate approximation of the transverse leakage. 
This code has been benchmarked for Cartesian, cylindrical and hexagonal geometry. NEM is coupled with the Penn State versions of TRAC-PF1 and TRAC-BF1.
Nestle
NESTLE is a multi-dimensional neutron kinetics code developed at North Carolina State University which solves the two or four group neutron diffusion equations in either Cartesian or hexagonal geometry using the nodal expansion method and the non-linear iteration technique. Three, two, or one-dimensional models may be used. Several different core symmetry options are available including quarter, half, and full core options for Cartesian geometry and 1/6, 1/3, and full core options for hexagonal geometry. Zero flux, non-reentrant current, reflective, and cyclic boundary conditions are available. The steady-state eigenvalue and time dependent neutron flux problems can be solved by the NESTLE code. The new Border Profiled Lower Upper (BPLU) matrix solver is used to efficiently solve sparse linear systems of the form AX = B. BPLU is designed to take advantage of pipelines, vector hardware, and shared-memory parallel architecture to run fast. BPLU is most efficient for solving systems that correspond to networks, such as pipes, but is efficient for any system that it can permute into border-banded form. Speed-ups over the default solver are achieved in RELAP5-3D© running with BPLU on multi-dimensional problems, for which it was intended.

Parcs USNRC version
PARCS is a three-dimensional reactor core simulator developed at Purdue University which solves the steady-state and time-dependent neutron diffusion equation to predict the dynamic response of the reactor to reactivity perturbations such as control rod movements or changes in the temperature/fluid conditions in the reactor core. The code is applicable to both PWR and BWR cores loaded with either rectangular or hexagonal fuel assemblies. 

The neutron diffusion equation is solved with two energy groups for the rectangular geometry option, whereas any number of energy groups can be used for the hexagonal geometry option. PARCS is coupled directly to the thermal-hydraulics systems codes TRAC-M and RELAP5 which provide the temperature and flow field information to PARCS during the transient. 
Quabox

QUABOX is a neutron kinetics code developed in the seventies at Gesellshaft fur Anlagen und Reaktorsicherheit (GRS) in Germany for 3D core neutron flux and power calculations in steady state and transient conditions. It solves the two groups neutron energy diffusion equation by the method of local polynomial approximation of the neutron flux.  

Example of coupled 3-D neutron kinetics and thermal-hydraulics codes

Among the three examples presented in  section 2.2.4 of Work Package 2 report, the case of SIMTRAN is briefly explained below.
SIMTRAN was developed as a single code merge, with data sharing through standard FORTRAN commons, of our 3D neutron kinetics nodal code SIMULA and the multi-channel, with cross-flows, thermal-hydraulics code COBRA-IIIC/MIT-2. Both codes solve the 3D neutron kinetics and TH fields with maximum implicitness, using direct and iterative methods for the inversion of the linearised systems.

SIMULA solves the neutron diffusion equations, in 1 or 2 groups, on 3D coarse-mesh nodes –quarter or full fuel assemblies- using our linear-discontinuous finite-difference scheme, where the interface net currents are given in terms of the actual node average and the corrected interface averaged fluxes, using synthetic interface flux discontinuity factors for each group and node-interface. SIMULA uses these synthetic coarse-mesh discontinuity factors, in the XY directions, pre-calculated by 2D pin-by-pin 2-group diffusion calculations of whole core planes. In the axial direction it performs embedded iterative 1D fine-mesh 2-group diffusion solutions for each node stack, with the radial leakage terms interpolated from the nodal 2-group solution.

COBRA-III-C/MIT-2, is a public code for thermal-hydraulics calculations, with implicit cross-flows, and homogeneous two-phase fluids. It is used worldwide for DNBR analysis in LWR sub-channels, as well as for 3D whole PWR core simulation with one or more channels per fuel assembly.

C.7  
Created Data Base and Transient Analysis Results

C.7.1 
Transients Suitable For Validation
The main objective of this section is to provide relevant guidelines for validation of neutron kinetics / thermal-hydraulic coupled models. This is accomplished by using measured data from NPP transients. The results of this subtask are explained in section 6 of the Work Package 1 report, ref. [1].

Although the transients and the data involved depend highly on the characteristics of the reference plant, these guidelines are meant to be general enough to determine if any transient of any plant could be used to validate the coupled codes.

The guideline is given on the basis of some cases used to exemplify the requirements that have to be met.

Obviously not all of the transients occurred in a plant are suitable to validate the coupled codes. Some requirements must be met, to insure, first of all, the quality of the data. Other requirements allow determining if using a coupled code to study them is appropriate. Among the first, it is necessary that the transients involved are correctly identified, temporally and with a description of the state of the plant where they occurred in the moment they did. To do so, the reactor where they occurred, the date and the time when they occurred, the core burn-up, power, average temperature, boron concentration and control rod position (banks D&C) at the moment they occurred have to be clearly stated. Eventually a manual action performed needs to be signalled. Moreover, the data need to be properly recorded, stating clearly the magnitude they measure and the units in which they measure it. This is valid both for data given in a time sequence or for “snapshots” of the state of the plant at a given time point.

The transients suitable to validate a coupled code have to show some evidence of feedback effects, caused by the occurrence of asymmetries or by any other reason.

The section 6 in ref. [1] reports specific data format and gives information on four different actual transients occurred in Ascó (PWR with UTSG), Oskarhamn 2 (BWR), Peach Bottom (BWR) and Three Mile Island 1 (PWR with OTSG).

The given information for each case is organized in four subsections: Plant description, Transient description, Measured data (neutron kinetics and thermal-hydraulics). Note that all these data are in general multidimensional and have to be given in a readable way; the specific format depends on the type of data.

These four transients are a good example of what is available for validating NPP models.

C.7.2 
Results from Available Calculations 

As an activity of CRISSUE-S project, a database of reference transient calculations has been prepared. Existing results have been put together and are explained in the Annex 1 of the WP2 report, ref. [2].

The main purpose of the effort is to constitute a database of results that can be used by analysts as well as by decision makers to get a ‘quantitative’ idea about expected transient scenarios and, definitely, to support decisions about the need to perform coupled calculations related to a generic NPP. 

Calculations have been performed utilizing computational tools and input decks developed and already utilized for different purposes (an overview is given in Tab. I, hereafter). Each calculation is documented by one page description and two pages of significant system related time trends or 3-D snap-shots of  core related quantities. The last section of the Annex 1, ref. [2] is devoted to the calculation of the enthalpy release to the fuel for some of the significant scenarios (i.e. for calculations that produced the highest local power excursion) documented in the previous sections of the same Annex. 

The following main limitations apply for the performed calculations:

· The cross section sets have been derived for a specific NPP status that does not coincide with the worst or the most critical status expected for the considered transient. As a consequence, the range of validity of the derived cross-sections may be over-passed when different transient are analysed (by adopting the same set of cross sections).  

· Although an effort has been made to achieve qualified results, a comprehensive check of the various qualification requirements has not been made, as already mentioned. Therefore, the reported results should be considered qualified as-far-as-possible.  This is true for stand-alone Relap5 or Parcs or Nestle input decks as well as for the coupled input decks.

· Actuation logics of all NPP systems that may have a role during the assigned transients have not been necessarily simulated.    

C.8 
Qualification Requirements

This section has to be considered strongly related to that of thresholds of acceptability (section 2). Computer codes require preparation of the mathematical model that can adequately simulate nuclear power plant or part of it or processes occurring. This mathematical model consists of the computer code itself, and set of input data grouped in file (or files) that substantially describe plant (or facility) within the boundaries and assumptions of the code models. Preparation of such a model is not only the source of the largest number of the errors, but also of  uncertainties that affect the use of best-estimate codes. The full knowledge of the computer code models is not sufficient for the error-free preparation of the nodalisation. It is well beyond the purposes of the project to discuss into detail code assessment requirements and related present status. However, some guidelines of acceptability are presented.

Neutron kinetics and thermal-hydraulic nodalisation requirements are summarized in the following paragraphs starting with the suitable level of detail of input deck.

In following subsection the thermal-hydraulic nodalisation development is discussed along with the acceptability of the nodalisation at both the steady state level and the on-transient level.

The remaining two subsections have less detail due to the fact that the neutron kinetics and the coupling qualification processes are not as advanced as the thermal-hydraulic one.  

C.8.1 
Suitable Level of Detail for Input Deck
Nodalisations that allow the evaluation of neutron kinetics cross section, 3-D neutron kinetics and thermal-hydraulic nodalisations should be distinguished, as already mentioned. Various ‘degrees of freedom’ are left to the user when setting up nodalisations for performing the simulation of a requested transient in an assigned system. Recommendations hereafter consider the capability of current computers (year 2003) and aim at reducing the user effect (or the ‘degrees of freedom’).

· Nodalisations for CSC, THSC and NKC must be consistent: the same elementary cell must be considered in each application.

· Individual fuel elements (minimum level of detail) should be considered in each of the concerned code. These typically differ among each other for burn-up and initial enrichment, presence of burnable poison and of control rod, position in the core and (in some cases) for the number of rods.  

· Lumping together ‘similar fuel’ elements, typically in the THSC nodalisations, should be avoided as much as possible.

· ‘Symmetry’ assumptions must be justified and applied in similar way for the various codes.

· Axial node sub-divisions in the order of twenty (or greater) must be adopted: i.e. each fuel assembly must be divided into 20 or more parts, typically equal in terms of axial length.

· In THSC nodalisation, the level of detail of different parts of the RPV should be consistent with the level of detail of the core region.

· Energy ranges for neutrons must be the same for CSC and NKC nodalisations.

· Care must be taken in identifying the range of variation (validity) of cross section from the CSC calculation. It must be ensured that those limits are not over-passed in the THSC-NKC coupled calculation. 

· The core bypass (typical THSC nomenclature) and the reflector (typical NKC nomenclature) nodalisation must be consistent in the various step of the coupled calculation (e.g. volume of the core bypass, input parameter for THSC, must be consistent with the reflector thickness utilized in the NKC input deck).   

C.8.2 
Qualification of TH Nodalisations and Codes
Thermal-hydraulic nodalisations (input deck) development  

Four fundamental pre-conditions shall be fulfilled for the correct application of a complex thermal-hydraulics system code to the prediction of transient scenarios expected in NPP: 

· The code should be frozen.

· The code should be properly qualified through wide, preferably international, assessment program, as already mentioned.

· The developer of the nodalisation should be a qualified code user for the selected code. 

· The nodalisation (of the plant) once developed should be properly qualified.

Engineering judgment is normally used to a wide extent to develop an input deck. The importance of establishing a procedure for the nodalisation set-up and qualification is a consequence. Such a procedure can be split into the following steps: a) gathering of a verified set of NPP data b) set-up of the plant nodalisation (input deck for the nominal steady state conditions), c) qualification of the nodalisation.

A nodalisation can be considered as qualified when 1) it has a geometrical fidelity with the involved plant, 2) it is reproducing the nominal measured steady-state condition of that plant, 3) it shows a satisfactory behaviour in time-dependent conditions, that is according with the time-dependent data of any test performed, or if available, of any actual transient in the nuclear power plant. Therefore, qualification of the nodalisation has been divided in two separate processes: steady state and on-transient.

Acceptability of the nodalisation at the steady state level

In order to address the last question, the University of Pisa proposed a number of ‘acceptability conditions’ that are summarized in Work Package 2 report and the related references. These conditions have been adopted since more than ten years at the time of issuing of the present report. 

Two sets of conditions can be distinguished: the former (i.e. rows 1 to 11 in Table II) deals with ‘the values of the quantities’ that are part of the input deck, the latter (i.e. rows 12 to 25) deal with the results predicted by the code at the end of the steady state calculation.
Acceptability of the nodalisation at the on-transient level 

The demonstration of the nodalisation quality at the steady state level does not ensure that the prediction of a transient scenario is correct from a phenomenological point of view, or even that the nodalisation (input deck) is free of errors. Errors can be part of an input deck that has been qualified at the ‘steady-state’ level. In order to achieve the full qualification the developed NPP input deck, already qualified at the steady state level (following section 2.4.1.1) must undergo to the on-transient nodalisation qualification process. 

This is aimed at reproducing (or simulating) one or more transient scenarios in Integral Test Facilities (ITF) that have ‘similar’ characteristics as the scenarios that constitute the objective for the NPP related application.  In other words, the NPP nodalisation must be used to predict a experimental scenario. This is achieved through the so- called ‘Kv-scaled’ procedure suitable to derive input boundary conditions for the NPP nodalisation, and to evaluate the comparison between NPP predictions and ITF data.

Quality demonstration for the output of the ‘Kv-scaled’ calculation is obtained from the qualitative and quantitative accuracy evaluation, adopting suitable analytical tools.

The ‘Kv-scaled’ calculation may be substituted by a proper benchmark activity, where NPP calculation results are compared with results of other qualified nodalisations and by performing the evaluation of suitable operational transients in relation to which data from the concerned NPP are available. 

C.8.3 
Qualification of Neutron-Kinetics Nodalisations and Codes
The qualification process of neutron-kinetics nodalisations and codes is not as advanced as in the thermal-hydraulic field and so the statements and ideas discussed shall not be considered as a final solution of the issue.

Neutron kinetics nodalisation (input deck) development and qualification 
In order to achieve a neutron kinetics nodalisation a much smaller number of code-user decisions and choices is needed in comparison with a thermal-hydraulics nodalisation. This can be easily understood by considering that only the core is concerned and makes more straightforward the process of developing a 3D neutron kinetics nodalisation. 

Nevertheless, the generic recommendations given in section 2.4 and the acceptability criteria discussed in relation to thermal-hydraulics nodalisation (sec. 2.4.1), can be translated into a number of preliminary requirements.

A first group of requirements (nodalisation development) includes the identification of

· The core array matrix (square, triangular, plate, etc.).

· The variety of fuel elements or fuel assemblies (FA) that constitute the core.

· The variety of fuel rods that constitute each FA (burnable poisons, etc.).

· The relative position of control rods (CR) and FA and of fuel rods, as needed.

· The role of the ‘fluid-dynamic’ core bypass and of the neutron kinetics ‘reflector’ including massive structures in radial and axial positions (barrel, fuel boxes, core support plates, etc.).

Ranges of validity of parameters, namely of cross sections, should be compared with ranges of variations expected during the transient calculation. Thermal-hydraulics input parameters (needed by the stand-alone 3D neutron kinetics codes) should be properly identified and consistently fixed. User choices, including ADF, Xenon consideration, shall be properly justified, together with the selected value of the time step. Reproduction of ‘reference-code-runs’ is recommended, before any use of the code.

C.8.4 
Coupling Qualification
There are certain requirements to the coupling of thermal-hydraulic system codes and neutron-kinetics codes that ought to be considered. The objective of these requirements is to provide accurate solutions in a reasonable amount of CPU time in coupled simulations of detailed operational transient and accident scenarios. These requirements are met by the development and implementation of six basic components of the coupling methodologies:

1. Coupling approach – integration algorithm or parallel processing

2. Ways of coupling - internal or external coupling

3. Spatial mesh overlays
4. Coupled Time-Step Algorithms
5. Coupling Numerics – Explicit, Semi-Implicit and Implicit Schemes
6. Coupled Convergence Schemes
Different international exercises, mainly benchmarks, have been organized with the aim of providing a basic level of qualification of the tools utilized for the analysis. Recent OECD-NEA/NSC benchmarks have played an important role in fulfilling the purpose of qualifying the coupling methodologies.
C.9 
Licensing Status

Since one of the CRISSUE-S project objectives is preparing a state of art report, the section devoted to licensing is organized according with this aim. In this sense Work Package 2 report establishes the licensing status in different countries and focuses on the items in which coupled codes are currently used to solve licensing issues. These are: the ATWS issue, the BWR stability, and the ‘prescribed’ RIA analysis Low Power.

The three issues are explained in the main report with emphasis to the acceptance criteria, applied list of quantities and threshold values acceptable to different regulatory bodies. The purpose of the section is to give an idea of the current status of the interaction between the regulatory requirements and the coupled 3D neutron kinetics thermal-hydraulics techniques.

The ATWS issue

Anticipated Transients Without Scram (ATWS) are anticipated operational occurrences followed by the failure of one reactor scram function. Available transient analyses of ATWS events indicate that WWER reactors, like PWR, have the tendency to shut themselves down if the inherent nuclear feedback is sufficiently negative. Various control and limitation functions of the WWER plants also provide a degree of defence against ATWS.  

The interpretation of the ATWS rules may vary dependent on country and reactor type. For example, there are not any specific ATWS rules in effect in Sweden since the probability for ATWS in was considered to be very low because of the possibility to insert control rods by electrical motors in addition to the fast hydraulic insertion. The Swedish BWR also have a manual boron system. The primary objective of the boron system is to keep the system sub-critical in the case that several adjacent control rod s can not be fully inserted.

The electrical control rod insertion system and the boron system do not fulfil all requirements that exist on safety systems and new regulations are being discussed. The final proposal will probably be that all anticipated transients during plant lifetime should be analysed with respect to failure to scram. The success criteria will be that of the design basis accidents i.e. fuel melting, cladding temperature and oxidation, and integrity of the pressure boundary. 

Acceptance criteria (ATWS)
In general, ATWS acceptance criteria are comparable to the criteria for the postulated accidents and address primary system integrity, fuel cooling capability, shutdown reactivity, and off-site radiological consequences. In particular:

International practice accepts less restrictive reactor coolant system (RCS) pressure limits for ATWS. ATWS limits are generally based on allowable stress limits for ASME Service level C or 135 % of design pressure (for WWER-1000 reactors, this is also the primary circuit hydro test pressure).

Fuel cooling capability should be demonstrated, i.e. core damage and calculated changes in core geometry do not prevent long term core cooling. However, there is no international consensus as to acceptance criteria.

The analysis of  ATWS events should demonstrate that a safe and stable shutdown of the reactor is achieved. Common international practice is to accept a sub-criticality of one percent as an adequate indication of reactor shutdown.

For radiological assessment, a general accepted approach is to assume that fuel cladding failure (leakage) occurs for all fuel rods having a potential for boiling crisis, e.g. having a DNBR less than the value that gives 95% probability at 95 % confidence level that DNB does not occur. It has not been necessary to apply less conservatism such as to demonstrate that site boundary limits for postulated accidents are not violated.

The BWR stability issue

The stability of BWR reactor systems have been a concern from the very beginning and extensive experimental and theoretical studies have been performed in order to design a stable fuel and core configuration. The requirement of stability is expressed in the general design criteria for nuclear power plants as:  “The reactor core and associated coolant, control, and protection systems shall be designed to assure that power oscillations which can result in conditions exceeding specified acceptable fuel design limits are not possible or can be reliably and readily detected and suppressed”.  

The problem seemed to be solved for a long time and no oscillation occurrence was experienced in BWR for several years. Since then a number of fuel and core design changes have been performed and also the power densities of the core have increased. Indications appeared in the late 80’s that instability may still be a problem. Instability events had been observed in TVO-1 and Forsmark 1 (1987) and later also in LaSalle(1988). After this authorities in all countries required a review of the stability features of their BWR. All authorities include analyses in the safety analysis reports. Authorities in some countries required changes in the procedures and plant safety systems. In other countries recommendations were made. In many cases the stability question is an integral part of the reload analyses using advanced methodology. Such technology is not generally used and in many cases only engineering judgement is available. For other reactors possible exclusion regions are identified by measurements as a part of the start-up procedure. 

Authorities have also emphasised the importance of training the operators to handle instabilities. One problem with this is that the computer programs full scope simulators can not truly simulate occurrence of instability, a fact which also calls for development of improved simulation methods for operator training. 

The major safety concern associated with instability is the cooling of the fuel and cladding integrity. One safety concern is if large undetected reactivity insertions take place for instance during regional oscillations. In cases where the two halves of the core oscillate are in opposite phase, the oscillation may not always show up in the APRM-signal, which is used by the reactor protection system. It has also been observed that severe un-damped oscillations may occur as a result of other kinds of transients such as for instance feed-water transients. Of importance is also the case where external disturbances occur at or near the resonance frequency of the core.

Modern technology in the control room may also make detection of instability more difficult. At one Swedish plant digital instrumentation had been introduced which prevented detection of instability although the amplitudes were large. Therefore dedicated stability monitors are in many cases used to give the operators a warning when unstable areas are approached. 

In the long term modifications in the protection systems are under consideration in many countries. These modifications should ensure that the reactor instrumentation and protection system can reliably protect the core against all kinds of instability without being wrongly activated under other circumstances. 

Acceptance criteria (BWR Stability)

One important parameter which characterizes the stability features of a reactor is the decay ratio. The decay ratio is a measure for how quick a perturbation of the reactor will die out. Limits of maximum allowed decay ratios in the core design are used in many cases. Such limits express the uncertainty associated with the specific method used and may vary between reactors and applications. Such maximum limits have also in the past in many cases been specified by the regulators.

Since it has been realized that regional oscillations is a more of a safety concern various kinds criteria are being developed to be able to reliably detect and suppress such occurrences. Such criteria or algorithms are parts of commercial products and not generally available.

The overall concern is the possibility for fuel failure. One acceptance criterion is therefore to ensure that dry-out of the fuel does not occur. Another criterion may be to ensure that rewet does occur after a dry-out of so short duration that fuel failure does not occur. 

The RIA issue and the events to be considered

A description of methodology used when analysing control rod ejection belonging to the group of reactivity initiated accidents is given. The first part is focused on the methodology used by Westinghouse for rod ejection analysis in Temelin NPP. The second part is devoted to the methodology used by Vuje-Trnava (Slovakia) for control rod ejection analysis in Bohunice NPP.  Within this framework, the essential conclusions valid for WWER control rod ejection analysis, taken from the IAEA guidance, are accounted for and described.
The list of events required to analyse by Czech Instructions and by US NRC RG 1.70 can be found in Work Package 2 and the related references.
Acceptance criteria (RIA)

The rod ejection event is classified as a postulated accident. Postulated accidents are of such low frequency (<10-2/year) such that they are not expected to occur, but considered in the design. Acceptance criteria are listed hereafter:

· Average fuel pellet enthalpy at the hot spot shall remain below a certain limit which may be dependent on fuel burn-up. This criterion ensures that core coolability is maintained.

· Average clad temperature at the hot spot shall not exceed a certain limit and the oxidation of Zirconium should be less than a certain fraction of the amount. This criterion ensures that clad melting and excessive clad embrittlement is avoided.

· Peak reactor coolant pressure shall remain at a value lower than the value which could cause stress to exceed the faulted condition stress limits. This criterion ensures that the structural of the reactor coolant boundary is not threatened. 

· Fuel melting limited to less than a certain fraction of the fuel volume at the hot spot, even if the average fuel pellet enthalpy is below the limits of criterion 1 above. This criterion ensures that fuel dispersal into the coolant will not occur.

C.10  
Use by Industry

The nuclear power industry, as being license holder of NPP, has to evaluate safety related critical issues for their existing plants, for instance in case of core reloading, planned power up-rating, or as part of required analyses of occurred events. As the existing plants have well established licensing procedures, including well founded analysis methods, the application of new innovative analysis methods have to be thoroughly evaluated, with specific emphasis to the capabilities of producing results that in general terms might be beneficial related to the NPP operation.  

Each licensing process related to a specific plant, includes the analyses of specific transients that can become crucial depending on the selected core state, dependent on used core fuel loading pattern, on burn-up, and in general terms on the reactor operational history. In view of most fruitful and beneficial applications, any innovative analysis method should preferably focus on such crucial transients. Currently, in PWR licensing process for instance, 4 or 5 licensing transients belong to this group, and do need the NK-TH coupled evaluation to fully explore the NK-TH interactions and associated influences on safety margins.

Every analysis method used in the licensing processes must be well founded and must have proven its capability in providing acceptable safety margins (best estimate or conservative) both from the license holder as well as from the nuclear safety authority perspective. A general applicable role in relation to nuclear safety of existing plants is that any modifications in the plant and/or in the applied licensing analysis methods have to reveal at least retained safety margins. When using new analysis methods a comprehensive validation data base must confirm the adequacy of the methods and also, in cases of best estimate methods, provide information of associated uncertainties in calculated values. With the new NK-TH coupled analysis methods provisions are at hand to accurately estimate the actual safety margins, which could provide incentives to more efficiently utilize the fuel and obtain cost benefits in the operation of the NPP, while still preserving and possibly also improving the safety. It is also envisioned that the coupled T-H/neutron kinetics analyses could provide more detailed insight in the basis used at the specification of operational procedures and could provide guidelines for optimisations of EOP.
Whence, if the feasibility of a licensing process including new analysis methods is of high priority of the industry, the possibility of gaining margins is closely related. An adjusted margin evaluation normally results in a more flexible cycle scheme and as a consequence a more efficient use of fuel.

Preserving technical knowledge and competence in the fields needed for engineering support of operating plants is currently of utmost importance for the responsible organizations of NPP operations. In the context of deregulation and an open market for distributing electrical power, utilities are facing this issue as the conservation of an “investment” performed over the years. In this sense any innovation on coupled NK-TH analysis can be even more acceptable if it has a feature of using previous experience to support future studies thus incorporating already gained knowledge.

In order to efficiently pursue coupled NK-TH analyses there is an obvious need of more profound organizational capabilities than those coming with the mere symbiosis of neutron-kinetic experts with TH-safety experts. It can be envisioned that a well coordinated team of both types of specialists will take advantage of a helpful synergy to deal with common subjects. If this point is fulfilled the results of any coupled analysis will thus be less dependent on any single user effect providing an increased adequacy. State of the art studies of any related subject are normally much welcomed with the important intention to take advantage of the main findings of such studies. This point applies not only to critical issues and subjects of first priority, but also on non critical issues related to the every day plant operation. 

Utilities are often in a position of having more than one alternative for the general control and quality assurance of calculations and results, especially in cases related with nuclear safety or with fuel management. The use of alternative analysis methods or computer codes, developed in an independent framework, can provide benefits when comparing results of the calculations performed by designers using licensing codes. 

In core design, interaction between the core design team and an engineering team having developed an alternative method can be of great importance with regard to cycle charging scheme optimisation and also to allowing validation of the performed calculations. In addition, this feedback is regarded by the regulatory authority as a proper procedure for the utility to verify the results based on benchmarks against a methodology that uses alternative tools.

Safety is strongly integrated in the NPP operation and has to be regarded as an ever present natural ingredient of the normal day to day operation activities. The NPP operation is strongly related to system and fuel design, control system design, and general plant engineering, and has to properly account for nuances in associated properties. That is why flexibility concerning the above mentioned every day subjects are very important from a utility standpoint. Such subjects are crucial when safety conclusions are applied and, definitely, they can also take advantage of coupled NK-TH analysis results. Coupled codes prove to be powerful tools that help to improve the understanding of the phenomena taking place in the power plants, and provide realistic boundary conditions for system studies related to plant operation.

Today in some PWR, discharge burn-up has reached more than 50000 MWd/T and some tests performed at special locations in commercial reactor cores have brought test fuel assemblies to a discharge burn-up of almost 70000 MWd/T. The interest of the industry for high burn-up is a reality. In a near future, an even higher burn-up will be considered and probably used, most likely along with new types of fuels. New analytical tools have to be compatible with the use of such fuels. These tools have to realize their application facing the complete problem, including fuel pin performance and the tight interaction between core neutron kinetics and thermal-hydraulics. The validation has to be thoroughly pursued and in order to be meaningful the analyses should be accompanied by associated uncertainty analyses to reveal more closely the actual safety margins.

CONCLUSION

A detailed description on CRISSUE-S project objectives fulfilment can be found mainly on last chapter of Work Package 2 report. This last section of Work Package 3 report is intended to emphasize on one hand the main findings of the project and on the other hand the open items that will explicitly or implicitly produce relevant recommendations for future.

Competing techniques discussion and the advancement of the state of the art have been treated deeply and reported with detail characterizing the involved phenomena, establishing the availability of tools and databases, and identifying areas of application as well as limitations. 

The project has provided a fruitful opportunity of wide cooperation between industry, utilities, regulators, and research institutions, and between European and Northamerican Countries. It has also promote the dialogue and collaboration between users of different technologies. Besides a deep interchange with VALCO project, CRISSUE-S has also had an interesting dialogue with organizations like TEPCO, NUPEC and PSI who attended at least one CRISSUE-S meeting as observers and have been informed of the progress of the project.

A fruitful connection has been established also with the NSC and the GAMA group of OECD as well as the IAEA.     

Participant utilities have allowed a limited but significant use of NPP measured data to check the qualification of the tools involved in the analysis.   

The project has also managed to produce results in harmony with on-going or proposed international programs like:   

· Benchmark on NUPEC BWR Full Size Bundle Test (proposed by NEA/NSC)

· Benchmark on WWER-1000 Coolant Transient (supported by  NEA/NSC and NEA/CSNI)

· Assessment of the Interface between Neutron Kinetics, Thermal-Hydraulics, Structural and Radiological Aspects in Accident Analysis (launched by IAEA)

· VALCO project (EC funded project in the Fifth Framework Program) 

The most significant aspects of the main issues like thermal-hydraulics, neutron-kinetics, the role of fuel, the regulatory position or general databases of both results npp data, are covered by CRISSUE-S. Although operator training seems to be subject not 100% integrated in the process of getting suitable analytical results, the project has also identified its relevance in cases of RIA.

Main Findings

The connections or the links existing among a number of subjects (e.g. derivation of neutron cross section, BWR stability, numerical solution methods, fuel modelling) that have been separately treated in the recent past has been shown. This may be seen as the first finding from the activity and streamlines the need to pursue an interdisciplinary approach in the future for the concerned subjects.   

Capabilities of 3D thermal-hydraulic computational tools: Codes are considered here that allow the 3D ‘porous media’ modelling approach (i.e. those codes that do not have the capability of predicting the local turbulence associated phenomena like the velocity or temperature profile inside a cross section). The conclusion is that these code are available and ready to be used but their qualification level is not acceptable.

List of transients in relation to which analysis is recommended: The prediction of NPP scenarios constitutes the final goal of coupled neutron kinetics thermal-hydraulics techniques. However, the full exploitation of those techniques implies streamlining their use and recommendations for this. Therefore transients have been selected within the present framework whose analysis is recommended by coupled techniques. Distinction has been made between BWR, PWR and VVER and only the PWR related list of transients is proposed hereafter. This includes: 

· MSLB. 

· LOFW-ATWS. 

· CR-expulsion. 

· LBLOCA-DBA.   

· Incorrect Connection (start-up) of an Inactive (idle) Loop. 

· MSLB-ATWS. 

· SBLOCA-ATWS. 

Identification of thresholds of acceptability: Answering the question ‘how good is good enough’ constitutes the old huge task that cannot be solved once for ever. The progress of science moves always farther the acceptability of any technological product including the results of code applications to nuclear reactor safety. However, an attempt has been made, ref. [2] to fix acceptable targets for calculation precision, distinguishing between (acceptable) quantity and  time errors. The considered values give an  idea of the current capabilities of computational tools, provided qualification methods are adopted. Four examples of acceptability thresholds from more than a dozen considered in ref. [2]:

· For pressure pulses characterized by FWHM < 0.1 s acceptable error is 10 % nominal pressure,

· For core power pulses characterized by FWHM < 0.1 s acceptable error is 100% nominal power or 300% initial power, whatever is smaller,

· For core power pulses characterized by FWHM ( 0.1 s, acceptable threshold error is 20% nominal power or 100% initial power, whatever is smaller,

· The acceptable time error that can be associated to the prediction of time of occurrence of pressure or core pulse is 100% of the best estimate value.

Acceptability of neutron kinetics calculation shall be consistent with discrepancies in the application of state of the art codes to reference problems. Errors in predicting k-eff (or k() of the order of 3-4% appear acceptable.    

Relevance of the role of fuel: The minor role of the fuel within the coupled neutron kinetics thermal-hydraulic environment was noted. Actually, transient modelling of  fuel performance must become the third ring of an ideal un-broken chain including the two other disciplines. Changes of fuel geometric and physical properties are expected during RIA and must be properly accounted for in the modelling. For instance in case of local power increase fuel fragmentation and release of fission gases may have an effect upon neutron kinetic cross section as well as upon the thermal properties of the gap and of the fuel itself. The feedback in terms of neutron power and of power transmitted to the coolant might be non-negligible. No approach deals with this phenomena at present.      
Uncertainty: Owing to a large number of reasons discussed in the report, the results from coupled 3D neutron kinetics thermal-hydraulic calculations are not precise. Therefore, uncertainty must be connected with any prediction. Two main findings outcome from the performed activity. The first one is connected with the demonstration that the ‘Internal Assessment of Uncertainty’ method, based upon the interpolation of the detected accuracy is applicable for coupled techniques even though relevant resources are necessary to develop a suitable error database. The second one is connected with the identification of the main sources of uncertainty. These can be summarized as follows:

· Sub-cooled HTC, namely in transient conditions characterized by ‘large’ time derivative for the produced power. 

· Pressure wave propagation inside the complex vessel geometry when single phase of two phase fluid is present. 

· Effect of (prompt) radiolysis upon neutron cross section following fast transients.

· Effect of direct energy release to the coolant following a fast transient. 

· Detailed specifications about mechanical components such as valves and control rods. The function valve net cross sectional flow area versus time during opening or closure events is irrelevant for the majority of thermal-hydraulic transients, but may become important when neutron kinetics feedback is computed. Analogously, the velocity as a function of time during a control rod expulsions transient is relevant (i.e. not only the total expulsion time).

· Parameters connected with fuel must be calculated during RIA transient allowing proper feedback (e.g. neutron kinetic cross section and thermal parameter, like gap thickness and conductivity should be calculated as a function of time and provide suitable feedback for the power evaluation). 

Uncertainty sources connected with the selected neutron kinetics parameters are also discussed in  ref. [2]. As examples rod worth, fraction of delayed neutron and Doppler coefficients are typically defined with uncertainties given by ( 10%, ( 5% and ( 20%, respectively.

Licensing status: The main finding is that great attention is paid by regulatory bodies toward issues like control rod expulsion and ultimate fuel resistance. However, the importance of the use of  coupled  3D neutron kinetics thermal-hydraulic techniques is not recognized. Making reference to the ATWS issue, the survey of the regulatory position in eight Countries, brings to the following additional main findings:

· ATWS analyses are mandatory (i.e. foreseen in the licensing process) in a small number of Countries compared with the number of Countries that were taken into consideration. However, generic safety analyses are performed in almost all Countries to address the issue.

· The attention toward coupled 3D neutron kinetics thermal-hydraulic techniques from the regulatory bodies is insignificant in almost all cases.  

Created database: The database of results presented in the Annex I gives an idea of the transient behaviour of the selected NPP in cases when neutron kinetics thermal-hydraulic coupling is relevant and constitutes a reference  for those code users engaged in similar analyses.

New Frontier

New frontier for research or recommendations for future development can be derived from the performed analysis and, namely, from the items summarized in this chapter. Therefore, a straightforward list of recommendations is  

· Systematic qualification of the various steps of the process of the application of coupled neutron kinetics thermal-hydraulic techniques is needed, including the adoption of available tools and procedures.

· Full consideration shall be given to the identified sources of uncertainties (section above).

· It must be clear that results obtained by 0-D neutron kinetics coupled with thermal-hydraulics are not necessarily conservative. This observation must give the impulse for extended applications of coupled 3D neutron kinetics thermal-hydraulic techniques in the nuclear safety domain.

· The integration is needed of nuclear fuel related models into the neutron kinetics thermal-hydraulics coupling. This also includes the chemistry with main reference to the processes of crud formation and release.

· The industry and the regulatory bodies should become fully aware of the capabilities (and of the limitations) of the concerned techniques. It is expected that regulatory bodies consider the list of transients in LWR whose analysis is recommended by coupled techniques: BWR stability, ATWS and those transients characterized by asymmetric core behaviour are the most important. On the industry side, operators should be made aware of transients that are calculated by 3D coupled neutron thermal-hydraulic techniques and simulators, control rooms and EOP should benefit of the experience gained from the application of those techniques. 

The prepared database is a good starting point that can be improved and completed with the information of other databases or in connection with organizations like WANO.

The search of NPP data  performed in CRISSUE-S project in order to create the database helped clarifying future needs of data recording in commercial reactors. In this sense it is recommended to improve in-core parameters recording and to qualify such plant data both in PWR and BWR. 

Finally although industry faces safety related critical issues thinking mainly on realistic improvements on existing licensing procedures, utilities accept to take into account innovative methods when they do have the capability to produce a benefit in general terms.

As a consequence of the above paragraph, it seems mandatory to use these new techniques for the design of new generation plant.

Each licensing process is related to a specific plant, and has specific transients that become crucial depending on different aspects that are analysed in CRISSUE-S. Thinking on a fruitful application, any innovative method should focus on the analysis of crucial transients. 

Industry believes that gaining margins comes together with the improvement of licensing process and that improvements usually result in a better use of fuel.  

Having more than one alternative for the general check of calculations, mainly if they are related with safety or with fuel management and also conserving technical knowledge applied to the field of engineering support to operating plants are currently an important concern of the operation responsible that can be fulfil, for sure, if the conclusions of CRISSUE-S project are applied in a realistic basis and following the habits of technical dialogue between utilities, regulators, and research institutions used in the project.

A natural continuation of CRISSUE-S project is that developed by some of the partners and presented in POST-FISA Workshop 5 in November 13th, 2003 as “
US-EC Cooperation in State-of-the-Art Nuclear Safety Research – Pilot Project on Accident Analysis Codes and Uncertainty Analysis Methodology”. The scope of this 
project is intended deal to with: 

· Investigations on the completion of the uncertainty analysis methodology for coupled 3-D kinetics/thermal-hydraulics codes.

· Studies on improving coupled calculations by utilizing CFD results in the coarse-mesh thermal-hydraulics models.

· Investigations on extending modelling capabilities of coupled codes to provide predictions of local safety parameters (on pin level).

· Studies on modelling coupled neutron kinetics/thermal-hydraulic/mechanical phenomena.

· Investigations on extending uncertainty analysis for local (pin level) coupled code predictions.

A consolidation of the knowledge and technical background analysed in CRISSUE-S is expected from this development along with a wide application of the involved techniques to current and future power plants.

REFERENCES

[1] F. D’AURIA, A. BOUSBIA SALAH, G.M. GALASSI, J. VEDOVI, F. REVENTÓS, A. CUADRA, J.L. GAGO, A. SJÖBERG, M. YITBAREK, O. SANDERVÅG, N. GARIS, C. ANHERT, J.M. ARAGONÉS, G. VERDÙ, R. MIRÒ J. HADEK, J. MACEK, K. IVANOV, RIZWAN-UDDIN, E. SARTORI, U. RINDELHARDT, U. ROHDE, W. FRID, D. PANAYOTOV, Neutron Kinetics / Thermal-Hydraulics Coupling in LWR Technology: Data Requirements and Databases Needed for Transient Simulations and Qualification - CRISSUE-S WP1 Report,

University of Pisa Report, DIMNP NT 519(03), Pisa, Italy, December 2003

[2] F. D’AURIA, A. BOUSBIA SALAH, G.M. GALASSI, J. VEDOVI, F. REVENTÓS, A. CUADRA, J.L. GAGO, A. SJÖBERG, M. YITBAREK, O. SANDERVÅG, N. GARIS, C. ANHERT, J.M. ARAGONÉS, G. VERDÙ, R. MIRÒ J. HADEK, J. MACEK, K. IVANOV, RIZWAN-UDDIN, E. SARTORI, U. RINDELHARDT, U. ROHDE, W. FRID, D. PANAYOTOV, Neutron Kinetics / Thermal-Hydraulics Coupling in LWR Technology: State-Of-The-Art Report - CRISSUE-S WP2 Report,

University of Pisa Report, DIMNP NT 520(03), Pisa, Italy, December 2003

[3] F. D’AURIA, A. BOUSBIA SALAH, G.M. GALASSI, J. VEDOVI, F. REVENTÓS, A. CUADRA, J.L. GAGO, A. SJÖBERG, M. YITBAREK, O. SANDERVÅG, N. GARIS, C. ANHERT, J.M. ARAGONÉS, G. VERDÙ, R. MIRÒ J. HADEK, J. MACEK, K. IVANOV, RIZWAN-UDDIN, E. SARTORI, U. RINDELHARDT, U. ROHDE, W. FRID, D. PANAYOTOV, Neutron Kinetics / Thermal-Hydraulics Coupling in LWR Technology: Achievements and Recommendations Report CRISSUE-S – WP3 Report,

University of Pisa Report, DIMNP NT 521(03), Pisa, Italy, December 2003

Table I – Overview of analyses performed by coupled TH / neutron kinetics techniques within the framework of the CRISSUE-S project.
	ID
	Transient type
	Reactor type - Analyses ID  & Status

	
	
	PWR  Case Identity
	BWR Case Identity
	VVER Case Identity

	I
	MSLB
	Case 1-PWR: TMI (X)

Case 2-PWR: ASCO (X)
	-
	Case 1-VVER:VVER-1000 (X)

Case 2-VVER: VVER-440 (X)

	II
	LOFW – ATWS
	Case 3-PWR: TMI (X)
	-
	Case 3-VVER: VVER-1000 (X) 

Case 4-VVER: VVER-440 (*)

	III
	CR Ejection
	Case 4-PWR: TMI (X)
	Case 3-BWR: PB2 (X)

Case 4-BWR: PB2 CR bank Ejection (X)
	Case 5a-VVER: VVER-1000 (X)

Case 5b-VVER: VVER-1000 CR bank ejection (X)

Case 6-VVER: VVER-440 (*)

	IV
	LBLOCA-DBA
	Case 5-PWR: TMI(X)
	Case 9-BWR: PB2 (Y)
	Case 7-VVER: VVER-1000 (Y)

Case 8-VVER: VVER-440 (*)

	V
	Incorrect Insertion of an Inactive Loop
	Case 6-PWR: TMI (X)
	-
	Case 9-VVER: VVER-1000 (Y)

Case 10-VVER: VVER-440 (*)

	VI
	MSLB – ATWS
	Case 7-PWR: TMI (X)
	-
	Case 11-VVER: VVER-1000 (X)

Case 12 -VVER: VVER-440 (*)

	VII
	SBLOCA – ATWS
	Case 8-PWR: TMI (X)
	-
	Case 13-VVER: VVER-1000 SBLOCA (X)

Case 14-VVER: VVER-440 (*)

	VIII
	Turbine Trip
	-
	Case 1-BWR: PB2 (X)
	-

	IX
	Turbine Trip- ATWS
	-
	Case 2-BWR: PB2 (X)
	-

	X
	FW Temperature Increase
	-
	Case 5-BWR: PB2 (X)
	-

	XI
	MCP flow rate increase
	-
	Case 6-BWR: PB2 (X)
	-

	XII
	MCP flow rate increase-ATWS
	-
	Case 7-BWR: PB2 (X)
	-

	XIII
	BWR Stability
	-
	Case 8-BWR: PB2 (X)
	-

	IVX
	BWR Stability-ATWS
	-
	Case 9-BWR: PB2 (*)
	-


X: Analysis performed and documented

Y: Analysis performed and not documented

-: Analysis not applicable or not considered

*: Analysis not performed

Table II – Acceptability criteria for thermal-hydraulics nodalisation qualification at the ‘steady-state’ level.

	
	QUANTITY
	ACCEPTABLE ERROR (°)

	1
	Primary circuit volume
	1%

	2
	Secondary circuit volume
	2%

	3
	Non-active structures heat transfer area (overall)
	10%

	4
	Active structures heat transfer area (overall)
	0.1%

	5
	Non-active structures heat transfer volume (overall)
	14%

	6
	Active structures heat transfer volume (overall)
	0.2%

	7
	Volume vs. height curve (i.e. “local” primary and secondary circuit volume)
	10%

	8
	Component relative elevation
	0.01 m

	9
	Axial and radial power distribution
	1%

	10
	Flow area of components like valves, pumps and orifices
	1%

	11
	Generic flow areas
	10%

	(*)
	
	

	12
	Primary circuit power balance
	2%

	13
	Secondary circuit power balance
	2%

	14
	Absolute pressure (PRZ, SG, ACC)
	0.1%

	15
	Fluid temperature
	0.5% (**)

	16
	Rod surface temperature
	10 K

	17
	Pump velocity
	1%

	18
	Heat losses 
	10% 

	19
	Local pressure drops
	10% (^)

	20
	Mass inventory in primary circuit
	2% (^^)

	21
	Mass inventory in secondary circuit
	5% (^^)

	22
	Flow-rates (primary and secondary circuit)
	2%

	23
	Bypass flow rates
	10%

	24
	Pressurizer level (collapsed)
	0.05 m

	25
	Secondary side or downcomer level
	0.1 m


(°) The % error is defined as the ratio |reference value - calculated value| / |reference value|. The dimensional error is the numerator in the above expression.

(*) With reference to each of the quantities below, following a 100 s ‘transient - steady state’ calculation, the solution must be stable with an inherent drift < 1% / 100 s.

(**) And consistent with power error. 

(^) Of the difference between maximum and minimum pressure in the loop.

(^^) And consistent with other errors.

c)








PAGE  

